## 版本-Version
version number | Modify content |  | Modifier | modification time
版本号 | 修改内容 | Translation | 修改人 | 修改时间
V1.1 | 整理提交初版。 | Organize and submit the first version. |  | 2020.09.28
V1.2 | 修订部分flash存储参数、参数范围数据类型。 | Revise some flash storage parameters and parameter range data types. |  | 2020.11.02
V1.3 | 修订部分flash存储参数、参数命名。 | Revise some flash storage parameters and parameter naming. |  | 2020.11.12
V1.4 | 搜集所有需要用到的通信信息、参数，并进行分类整理。 | Collect all the communication information and parameters that need to be used, and classify them. |  | 2020.11.30
V1.5 | 新增地址对应的字节数 和 功能码匹配 | The number of bytes corresponding to the new address matches the function code |  | 2021.04.17
v1.6 | 实时运行信息2（PV+并网发电量）中单位0.1wh修改为0.1kwh | The unit of 0.1wh in real-time operation information 2 (PV + grid-connected power generation) is changed to 0.1kwh |  | 2021.05.07
| 电池当日充电量、电池当日放电量单位0.1wh修改为0.1kwh | The unit of the battery's current charging capacity and battery's daily discharge capacity is changed from 0.1wh to 0.1kwh.
| PV输入模式范围新增：2:无PV | New PV input mode range: 2: No PV
| 运行功能使能备注中B5与B6调换位置，修改B16为Forbid discharge enable，移除B17 | Change the positions of B5 and B6 in the running function enable remarks, modify B16 to Forbid discharge enable, and remove B17
| 修改并新增有功无功控制使能范围内容B3、B4、B5、 B6 、B7 、B8 | Modify and add active and reactive power control enable range content B3, B4, B5, B6, B7, B8
V1.7 | 新增 机器特性，用于平台识别类型 | Added machine characteristics for platform identification type |  | 2021.05.12
V1.8 | 电池总功率单位0.1V修改为1W | The total battery power unit is changed from 0.1V to 1W. |  | 2021.05.19
V1.9 | 额定视在功率单位1w修改为1VA | The rated apparent power unit 1w is modified to 1VA |  | 2021.05.19
| 总EPS无功功率单位VA修改为Var | The total EPS reactive power unit VA is changed to Var
| 新增最大交流输出电流单位 0.01A | Added maximum AC output current unit 0.01A
| 新增总并网有功功率单位W | Added total grid-connected active power unit W
| 新增总并网无功功率单位Var | Added new total grid-connected reactive power unit Var
| 新增总并网视在功率单位VA | Added total grid-connected apparent power unit VA
| 新增总负载有功功率单位W | Added new total load active power unit W
| 新增总负载无功功率单位Var | Added new total load reactive power unit Var
| 新增总负载视在功率单位VA | Added total load apparent power unit VA
| 新增PV总功率单位W | Added new PV total power unit W
| 新增R、S、T相电压直流分量单位mV | Added new R, S, T phase voltage DC component unit mV
| 新增R、S、T相GEN电压单位0.1V | Added R, S, T phase GEN voltage unit 0.1V
| 新增R、S、T相GEN电流单位0.01A | Added R, S, T phase GEN current unit 0.01A
| 新增R、S、T相GEN有功功率单位W | Added R, S, and T phase GEN active power unit W
| 新增总GEN有功功率单位W | Added total GEN active power unit W
| 新增总GEN无功功率单位Var | Added new total GEN reactive power unit Var
| 新增总GEN视在功率单位VA | Added total GEN apparent power unit VA
| 新增当日GEN发电量单位0.1kwh | Added daily GEN power generation unit of 0.1kwh
| 新增总EPS放电量单位0.1kwh | Added total EPS discharge unit 0.1kwh
| 新增总EPS充电量单位0.1kwh | Added total EPS charging unit 0.1kwh
| 新增总GEN发电量单位0.1kwh | Added total GEN power generation unit 0.1kwh
| 新增总电池充电量、总电池放电量单位0.1kwh | Added total battery charge and total battery discharge units of 0.1kwh
V2.0 | 修改机器特性表述问题 | Modify the problem of machine characteristics description |  | 2021.05.21
V2.1 | 额定视在功率修改为额定功率，单位：1VA修改为1W | The rated apparent power is changed to the rated power, and the unit: 1VA is changed to 1W. |  | 2021.06.23
| 新增参数读写03-06-10中的数据范围与单位 | Added new parameters to read and write the data range and unit in 03-06-10
| 添加数据范围-国家 | Add data range - country
V2.2 | 数据范围-国家修改 | Data Range-Country Modification |  | 2021.7.5
V2.3 | 运动功能使能参数设置中 “AC charge enable”修改为“Timing AC charge enable” “Forced charge enable”修改为“Timing charge enable” “Forced discharge enable”修改为“Timing discharge enable” “Forbid discharge enable”修改为“Timing Forbid discharge enable” | Motion function enable parameters are being set "AC charge enable" is changed to "Timing AC charge enable" "Forced charge enable" is changed to "Timing charge enable" "Forced discharge enable" is changed to "Timing discharge enable" "Forbid discharge enable" is changed to "Timing Forbid discharge enable" |  | 2021.7.15
V2.4 | “充放电功率”修改为“充放电功率指令” | "Charge and discharge power" is changed to "charge and discharge power command" |  | 2021.7.17
| “最大充电SOC”修改为“AC充电最大SOC”；“SocMaxChg”修改为“AcSocMaxChg” | "Maximum charging SOC" is modified to "AC charging maximum SOC"; "SocMaxChg" is modified to "AcSocMaxChg"
| “最小放电SOC”修改为“强制放电最小SOC”； | "Minimum discharge SOC" is changed to "forced discharge minimum SOC";
| 新增协议字段“强制充电最大SOC” | Added protocol field "forced charging maximum SOC"
| 新增协议字段“铅酸电池厂家” | Added new agreement field "lead-acid battery manufacturer"

## 运行信息04-Operation information 04
name |  | English | address | data type | Number of bytes | data range | unit | Remark |  | Whether to store | Revise
名称 |  | 英文 | 地址 | 数据类型 | 字节数 | 数据范围 | 单位 | 备注 |  | 是否存储 | 修改 |  | 0x03 | 0x04 | 0x06 | 0x10
协议头(机型属性信息) Protocol header (machine attribute information) | [9 empty] | 本页的存到ARM This page is stored in ARM |  |  | 功能码
机型名称 | Model name | InverName | 0-5 | U16*6 | 12 | [5 empty] | u16与U16书写统一一下。 | U16 and U16 writing should be unified. | X | √ | X | X
机器类型 | Machine type | InverType | 6 | U16 | 2 |  |  | 0-99 单相机 100-199 三相机 200-299 单相储能（包括裂相储能） 300-399 三相储能 | 0-99 single camera 100-199 Three cameras 200-299 Single-phase energy storage (including split-phase energy storage) 300-399 Three-phase energy storage |  |  |  | X | √ | X | X
额定功率 | Rated power | NormAppPower | 7-8 | U32 | 4 |  | 1W |  |  |  | 1. 1w修改为1VA; 2. 额定视在功率修改为额定功率，单位：1VA修改为1W | 1. 1w is modified to 1VA; 2. The rated apparent power is changed to the rated power, and the unit: 1VA is changed to 1W. | X | √ | X | X
额定输出无功功率 | Rated output reactive power | NormReactPower | 9-10 | U32 | 4 |  | 1var | [5 empty] | X | √ | X | X
硬件版名称 | Hardware version name | HardName | 11-14 | U16*4 | 8 | ASCII | [6 empty] | X | √ | X | X
硬件版本号 | Hardware version number | HardVer | 15 | U16 | 2 | [7 empty] | X | √ | X | X
协议名称 | Protocol name | ProtocolName | 16-19 | U16*4 | 8 | ASCII |  | “” |  |  |  |  | X | √ | X | X
协议版本号 | Protocol version number | ProtocolVer | 20 | U16 | 2 |  |  | XXX.XX |  |  | 从1开始 | Start from 1 | X | √ | X | X
主DSP软件名称 | Main DSP software name | MasterName | 21-24 | U16*4 | 8 | ASCII | [6 empty] | X | √ | X | X
主DSP软件版本号 | Main DSP software version number | MasterVer | 25 | U16 | 2 |  |  | XXX.XX |  |  |  |  | X | √ | X | X
副DSP软件名称 | Secondary DSP software name | SlaveName | 26-29 | U16*4 | 8 | ASCII | [6 empty] | X | √ | X | X
副DSP软件版本号 | Secondary DSP software version number | SlaveVer | 30 | U16 | 2 |  |  | XXX.XX |  |  |  |  | X | √ | X | X
HMI软件版名称 | HMI software version name | HMIName | 31-34 | U16*4 | 8 | ASCII | [6 empty] | X | √ | X | X
HMI软件版本号 | HMI software version number | HMIVer | 35 | U16 | 2 |  |  | XXX.XX |  |  |  |  | X | √ | X | X
CPLD软件版名称 | CPLD software version name | CPLDName | 36-39 | U16*4 | 8 | ASCII | [6 empty] | X | √ | X | X
CPLD软件版本号 | CPLD software version number | CPLDVer | 40 | U16 | 2 |  |  | XXX.XX |  |  |  |  | X | √ | X | X
逆变器SN | InverterSN | SerialNumber15-14 | 41 | U16 | 2 | ASCII | [6 empty] | X | √ | X | X
|  | SerialNumber13-12 | 42 | U16 | 2 | ASCII | [6 empty] | X | √ | X | X
|  | SerialNumber11-10 | 43 | U16 | 2 | ASCII | [6 empty] | X | √ | X | X
|  | SerialNumber9-8 | 44 | U16 | 2 | ASCII | [6 empty] | X | √ | X | X
|  | SerialNumber7-6 | 45 | U16 | 2 | ASCII | [6 empty] | X | √ | X | X
|  | SerialNumber5-4 | 46 | U16 | 2 | ASCII | [6 empty] | X | √ | X | X
|  | SerialNumber3-2 | 47 | U16 | 2 | ASCII | [6 empty] | X | √ | X | X
|  | SerialNumber1-0 | 48 | U16 | 2 | ASCII | [6 empty] | X | √ | X | X
国家 | nation | Country | 49 | U16 | 2 | 国家 | [6 empty] | X | √ | X | X
最大交流输出电流 | Maximum AC output current | MaxAcOutCurr | 50-51 | U32 | 4 |  | 0.01A |  |  |  | 新增单位 0.01A | New unit 0.01A | X | √ | X | X
机器特性 | Machine characteristics | InverCharacter | 52-53 | U32 | 4 |  |  | B0-B2: 0 代表并网机，1代表低压储能，2代表高压储能； B3-B5: 0 代表单相，1代表 裂相，2代表 三相； B6-B9: PV boost 路数，0代表1路，1代表2路，N代表N+路； B10：0 代表无发电机，1代表有发电机； B11-B31：reserved； | B0-B2: 0 represents grid-connected machine, 1 represents low-voltage energy storage, 2 represents high-voltage energy storage; B3-B5: 0 represents single phase, 1 represents split phase, 2 represents three phases; B6-B9: Number of PV boost channels, 0 represents 1 channel, 1 represents 2 channels, N represents N+ channels; B10: 0 means no generator, 1 means there is a generator; B11-B31: reserved; |  | 新增 21.05.12 用于平台识别 B1-B31 更改为 B11-B31 | Added 21.05.12 for platform identification B1-B31 changed to B11-B31 | X | √ | X | X
预留 | reserved | Reserve | 54-499 | [9 empty] | X | √ | X | X
实时运行信息1（PV+并网运行信息） | [12 empty] | X | √ | X | X
母线电压 | bus voltage | Vbus | 500 | U16 | 2 |  | 0.1V | 如果是单相,只有R相电压、R相电电流有效； 如果是俩相,只有R，S相电压、R,S相电电流有效； 如果三相四线制,表示：“X相电压”； 如果三相三线制,表示：“x-x 线电压”. 正表示逆变器往电网送电，负表示逆变器从电网取电 | If it is a single phase, only the R-phase voltage and R-phase electrical current are valid; If there are two phases, only R and S phase voltages and R and S phase electrical currents are valid; If the three-phase four-wire system is used, it means: "X-phase voltage"; If it is a three-phase three-wire system, it means: "x-x line voltage". Positive means the inverter sends power to the grid, negative means the inverter draws power from the grid. |  |  |  | X | √ | X | X
负母线电压 | Negative bus voltage | Vnbus | 501 | U16 | 2 |  | 0.1V | [5 empty] | X | √ | X | X
绝缘阻抗值 | Insulation resistance value | Riso | 502 | U16 | 2 |  | KΩ | [5 empty] | X | √ | X | X
漏电流有效值 | Leakage current effective value | IgfciRms | 503 | U16 | 2 |  | 1mA | [5 empty] | X | √ | X | X
R相直流分量 | R phase DC component | DCIR | 504 | S16 | 2 |  | 1mA | [5 empty] | X | √ | X | X
S相直流分量 | S phase DC component | DCIS | 505 | S16 | 2 |  | 1mA | [5 empty] | X | √ | X | X
T相直流分量 | T phase DC component | DCIT | 506 | S16 | 2 |  | 1mA | [5 empty] | X | √ | X | X
R相电网电压 | R phase grid voltage | VgridR | 507 | U16 | 2 |  | 0.1V | [5 empty] | X | √ | X | X
S相电网电压 | S phase grid voltage | VgridS | 508 | U16 | 2 |  | 0.1V | [5 empty] | X | √ | X | X
T相电网电压 | T phase grid voltage | VgridT | 509 | U16 | 2 |  | 0.1V | [5 empty] | X | √ | X | X
R相逆变电流 | R phase inverter current | IinvR | 510 | S16 | 2 |  | 0.01A | [5 empty] | X | √ | X | X
S相逆变电流 | S phase inverter current | IinvS | 511 | S16 | 2 |  | 0.01A | [5 empty] | X | √ | X | X
T相逆变电流 | T phase inverter current | IinvT | 512 | S16 | 2 |  | 0.01A | [5 empty] | X | √ | X | X
R相电网频率 | R phase grid frequency | FgridR | 513 | U16 | 2 |  | 0.01Hz | [5 empty] | X | √ | X | X
S相电网频率 | S phase grid frequency | FgridS | 514 | U16 | 2 |  | 0.01Hz | [5 empty] | X | √ | X | X
T相电网频率 | T phase grid frequency | FgridT | 515 | U16 | 2 |  | 0.01Hz | [5 empty] | X | √ | X | X
A相有功功率 | Phase A active power | PinvR | 516-517 | S32 | 4 |  | W | [5 empty] | X | √ | X | X
B相有功功率 | B phase active power | PinvS | 518-519 | S32 | 4 |  | W | [5 empty] | X | √ | X | X
C相有功功率 | C phase active power | PinvT | 520-521 | S32 | 4 |  | W | [5 empty] | X | √ | X | X
总有功功率 | total active power | Pinv | 522-523 | S32 | 4 |  | W | [5 empty] | X | √ | X | X
总无功功率 | total reactive power | Qinv | 524-525 | S32 | 4 |  | W | [5 empty] | X | √ | X | X
总功率因数 | Total power factor | PFinv | 526 | S16 | 2 |  | 0.001 | [5 empty] | X | √ | X | X
总视在功率 | total apparent power | Sinv | 527-528 | U32 | 4 |  | VA | [5 empty] | X | √ | X | X
R相并网功率（电表） | R-phase grid-connected power (meter) | PgridR | 529-530 | S32 | 4 |  | W | 正表示逆变器往电网送电，负表示逆变器从电网取电 | Positive means the inverter sends power to the grid, negative means the inverter draws power from the grid. |  |  |  | X | √ | X | X
S相并网功率（电表） | S-phase grid-connected power (meter) | PgridS | 531-532 | S32 | 4 |  | W | [5 empty] | X | √ | X | X
T相并网功率（电表） | T-phase grid-connected power (meter) | PgridT | 533-534 | S32 | 4 |  | W | [5 empty] | X | √ | X | X
总并网有功功率 | Total grid-connected active power | Pgrid | 535-536 | S32 | 4 |  | W |  |  |  | 新增单位W | Added unit W | X | √ | X | X
总并网无功功率 | Total grid-connected reactive power | Qgrid | 537-538 | S32 | 4 |  | Var |  |  |  | 新增单位Var | Add new unit Var | X | √ | X | X
总并网视在功率 | Total grid-connected apparent power | Sgrid | 539-540 | U32 | 4 |  | VA |  |  |  | 新增单位VA | Add new unit VA | X | √ | X | X
R相负载有功功率 | R phase load active power | PloadR | 541-542 | S32 | 4 |  | W | [5 empty] | X | √ | X | X
S相负载有功功率 | S phase load active power | PloadS | 543-544 | S32 | 4 |  | W | [5 empty] | X | √ | X | X
T相负载有功功率 | T phase load active power | PloadT | 545-546 | S32 | 4 |  | W | [5 empty] | X | √ | X | X
总负载有功功率 | Total load active power | Pload | 547-548 | S32 | 4 |  | W |  |  |  | 新增单位W | Added unit W | X | √ | X | X
总负载无功功率 | Total load reactive power | Qload | 549-550 | S32 | 4 |  | Var |  |  |  | 新增单位Var | Add new unit Var | X | √ | X | X
总负载视在功率 | Total load apparent power | Sload | 551-552 | U32 | 4 |  | VA |  |  |  | 新增单位VA | Add new unit VA | X | √ | X | X
PV总功率 | PV total power | Ppv | 553-554 | U32 | 4 |  | W |  |  |  | 新增单位W | Added unit W | X | √ | X | X
PV1电压 | PV1 voltage | Vpv1 | 555 | U16 | 2 |  | 0.1V | [5 empty] | X | √ | X | X
PV1电流 | PV1 current | Ipv1 | 556 | U16 | 2 |  | 0.01A | [5 empty] | X | √ | X | X
PV1功率 | PV1 power | Ppv1 | 557 | U16 | 2 |  | W | [5 empty] | X | √ | X | X
PV2电压 | PV2 voltage | Vpv2 | 558 | U16 | 2 |  | 0.1V | [5 empty] | X | √ | X | X
PV2电流 | PV2 current | Ipv2 | 559 | U16 | 2 |  | 0.01A | [5 empty] | X | √ | X | X
PV2功率 | PV2 power | Ppv2 | 560 | U16 | 2 |  | W | [5 empty] | X | √ | X | X
PV3电压 | PV3 voltage | Vpv3 | 561 | U16 | 2 |  | 0.1V | [5 empty] | X | √ | X | X
PV3电流 | PV3 current | Ipv3 | 562 | U16 | 2 |  | 0.01A | [5 empty] | X | √ | X | X
PV3功率 | PV3 power | Ppv3 | 563 | U16 | 2 |  | W | [5 empty] | X | √ | X | X
PV4电压 | PV4 voltage | Vpv4 | 564 | U16 | 2 |  | 0.1V | [5 empty] | X | √ | X | X
PV4电流 | PV4 current | Ipv4 | 565 | U16 | 2 |  | 0.01A | [5 empty] | X | √ | X | X
PV4功率 | PV4 power | Ppv4 | 566 | U16 | 2 |  | W | [5 empty] | X | √ | X | X
PV5电压 | PV5 voltage | Vpv5 | 567 | U16 | 2 |  | 0.1V | [5 empty] | X | √ | X | X
PV5电流 | PV5 current | Ipv5 | 568 | U16 | 2 |  | 0.01A | [5 empty] | X | √ | X | X
PV5功率 | PV5 power | Ppv5 | 569 | U16 | 2 |  | W | [5 empty] | X | √ | X | X
PV6电压 | PV6 voltage | Vpv6 | 570 | U16 | 2 |  | 0.1V | [5 empty] | X | √ | X | X
PV6电流 | PV6 current | Ipv6 | 571 | U16 | 2 |  | 0.01A |  |  |  | 对于储能，需要PV总功率 | For energy storage, total PV power is required | X | √ | X | X
PV6功率 | PV6 power | Ppv6 | 572 | U16 | 2 |  | W | [5 empty] | X | √ | X | X
PV连接状态 | PV connection status | PVConn | 573 | U16 | 2 | B0:CONNECTED B1:AVAILABLE B2:OPERATING B3:TEST | [6 empty] | X | √ | X | X
预留 | reserved | Reserve | 574-999 | [9 empty] | X | √ | X | X
实时运行信息2（PV+并网发电量） | [12 empty] | X | √ | X | X
逆变器当日发电量 | The inverter’s power generation for the day | EInvOutDay | 1000 | U16 | 2 |  | 0.1kwh |  |  | 存 | 单位0.1wh修改为0.1kwh | Unit 0.1wh changed to 0.1kwh | X | √ | X | X
逆变器当日从电网取电量 | The inverter draws power from the grid that day | EInvRecDay | 1001 | U16 | 2 |  | 0.1kwh |  |  | 存 |  |  | X | √ | X | X
当日到电网的电量 | The amount of electricity delivered to the grid that day | EtogridDay | 1002 | U16 | 2 |  | 0.1kwh |  |  | 存 |  |  | X | √ | X | X
当日取电网的电量 | Get electricity from the grid on the day | EfromgridDay | 1003 | U16 | 2 |  | 0.1kwh | [5 empty] | X | √ | X | X
当日到负载的电量 | The amount of electricity delivered to the load on the day | EtoLoadDay | 1004 | U16 | 2 |  | 0.1kwh |  |  | 存 |  |  | X | √ | X | X
当日取负载的电量 | Get the power of the load on the day | EfromLoadDay | 1005 | U16 | 2 |  | 0.1kwh | [5 empty] | X | √ | X | X
当日PV发电量 | PV power generation on the day | EPVDay | 1006-1007 | U32 | 4 |  | 0.1kwh |  |  | 存 |  |  | X | √ | X | X
当日PV1发电量 | PV1 power generation on the day | EPV1Day | 1008 | U16 | 2 |  | 0.1kwh |  |  | 存 |  |  | X | √ | X | X
当日PV2发电量 | PV2 power generation on the day | EPV2Day | 1009 | U16 | 2 |  | 0.1kwh |  |  | 存 |  |  | X | √ | X | X
当日PV3发电量 | PV3 power generation on the day | EPV3Day | 1010 | U16 | 2 |  | 0.1kwh |  |  | 存 |  |  | X | √ | X | X
当日PV4发电量 | PV4 power generation on the day | EPV4Day | 1011 | U16 | 2 |  | 0.1kwh |  |  | 存 |  |  | X | √ | X | X
当日PV5发电量 | PV5 power generation on the day | EPV5Day | 1012 | U16 | 2 |  | 0.1kwh |  |  | 存 |  |  | X | √ | X | X
当日PV6发电量 | PV6 power generation on the day | EPV6Day | 1013 | U16 | 2 |  | 0.1kwh |  |  | 存 |  |  | X | √ | X | X
逆变器总发电量 | Total power generated by the inverter | EInvOutTotal | 1014-1015 | U32 | 4 |  | 0.1kwh |  |  | 存 |  |  | X | √ | X | X
逆变器总从电网取电量 | The inverter always draws power from the grid | EInvRecTotal | 1016-1017 | U32 | 4 |  | 0.1kwh |  |  | 存 |  |  | X | √ | X | X
总到电网的电量 | Total power delivered to the grid | EtogridTotal | 1018-1019 | U32 | 4 |  | 0.1kwh |  |  | 存 |  |  | X | √ | X | X
总取电网的电量 | Total power taken from the grid | EfromgridTotal | 1020-1021 | U32 | 4 |  | 0.1kwh | [5 empty] | X | √ | X | X
总到负载的电量 | Total power delivered to the load | EtoLoadTotal | 1022-1023 | U32 | 4 |  | 0.1kwh |  |  | 存 |  |  | X | √ | X | X
总取负载的电量 | Take the total power of the load | EfromLoadTotal | 1024-1025 | U32 | 4 |  | 0.1kwh | [5 empty] | X | √ | X | X
总PV发电量 | Total PV power generation | EPVTotal | 1026-1027 | U32 | 4 |  | 0.1kwh |  |  | 存 |  |  | X | √ | X | X
预留 | reserved | Reserve | 1028-1499 | [9 empty] | X | √ | X | X
实时运行信息3（Backup运行信息） | [12 empty] | X | √ | X | X
R相电压直流分量 | R phase voltage DC component | DCVR | 1500 | S16 | 2 |  | mV | 如果输出类型是0,只有A相电压、A相电电流有效； 如果输出类型是 1,表示：“X相电压”； 如果输出类型是 2,表示：“x-x 线电压”. | If the output type is 0, only phase A voltage and phase A electrical current are valid; If the output type is 1, it means: "X-phase voltage"; If the output type is 2, it means: "x-x line voltage". |  | 新增单位mV | New unit mV | X | √ | X | X
S相电压直流分量 | S-phase voltage DC component | DCVS | 1501 | S16 | 2 |  | mV | [5 empty] | X | √ | X | X
T相电压直流分量 | T-phase voltage DC component | DCVT | 1502 | S16 | 2 |  | mV | [5 empty] | X | √ | X | X
R相EPS电压 | R phase EPS voltage | VepsR | 1503 | U16 | 2 |  | 0.1V | [5 empty] | X | √ | X | X
S相EPS电压 | S phase EPS voltage | VepsS | 1504 | U16 | 2 |  | 0.1V | [5 empty] | X | √ | X | X
T相EPS电压 | T phase EPS voltage | VepsT | 1505 | U16 | 2 |  | 0.1V | [5 empty] | X | √ | X | X
R相EPS电流 | R phase EPS current | IepsR | 1506 | S16 | 2 |  | 0.01A | [5 empty] | X | √ | X | X
S相EPS电流 | S phase EPS current | IepsS | 1507 | S16 | 2 |  | 0.01A | [5 empty] | X | √ | X | X
T相EPS电流 | T phase EPS current | IepsT | 1508 | S16 | 2 |  | 0.01A | [5 empty] | X | √ | X | X
R相EPS频率 | R phase EPS frequency | FepsR | 1509 | U16 | 2 |  | 0.01Hz | [5 empty] | X | √ | X | X
R相EPS有功功率 | R phase EPS active power | PepsR | 1510 | S16 | 2 |  | W | [5 empty] | X | √ | X | X
S相EPS有功功率 | S-phase EPS active power | PepsS | 1511 | S16 | 2 |  | W | [5 empty] | X | √ | X | X
T相EPS有功功率 | T-phase EPS active power | PepsT | 1512 | S16 | 2 |  | W | [5 empty] | X | √ | X | X
总EPS有功功率 | Total EPS active power | Peps | 1513-1514 | S32 | 4 |  | W |  |  |  | 离网并联时有功、无功也有可能是负值，相关的改成有符号数。 | When off-grid parallel connection, active power and reactive power may also be negative values, and the relevant ones should be changed to signed numbers. | X | √ | X | X
总EPS无功功率 | Total EPS reactive power | Qeps | 1515-1516 | S32 | 4 |  | Var |  |  |  | VA修改为Var | VA changed to Var | X | √ | X | X
总EPS视在功率 | Total EPS apparent power | Seps | 1517-1518 | U32 | 4 |  | VA | [5 empty] | X | √ | X | X
当日EPS放电量 | EPS discharge amount on the day | EepsInvDay | 1519 | U16 | 2 |  | 0.1kwh |  |  | 存 |  |  | X | √ | X | X
当日EPS充电量 | EPS charging amount on the day | EepsRecDay | 1520 | U16 | 2 |  | 0.1kwh |  |  | 存 |  |  | X | √ | X | X
R相GEN电压 | R phase GEN voltage | VgenR | 1521 | U16 | 2 |  | 0.1V |  |  |  | 新增单位0.1V | Added unit 0.1V | X | √ | X | X
S相GEN电压 | S phase GEN voltage | VgenS | 1522 | U16 | 2 |  | 0.1V | [5 empty] | X | √ | X | X
T相GEN电压 | T phase GEN voltage | VgenT | 1523 | U16 | 2 |  | 0.1V | [5 empty] | X | √ | X | X
R相GEN电流 | R phase GEN current | IgenR | 1524 | S16 | 2 |  | 0.01A |  |  |  | 新增单位0.01A | New unit 0.01A | X | √ | X | X
S相GEN电流 | S phase GEN current | IgenS | 1525 | S16 | 2 |  | 0.01A | [5 empty] | X | √ | X | X
T相GEN电流 | T phase GEN current | IgenT | 1526 | S16 | 2 |  | 0.01A | [5 empty] | X | √ | X | X
R相GEN有功功率 | R phase GEN active power | PgenR | 1527 | S16 | 2 |  | W |  |  |  | 新增单位W | Added unit W | X | √ | X | X
S相GEN有功功率 | S phase GEN active power | PgenS | 1528 | S16 | 2 |  | W | [5 empty] | X | √ | X | X
T相GEN有功功率 | T phase GEN active power | PgenT | 1529 | S16 | 2 |  | W | [5 empty] | X | √ | X | X
总GEN有功功率 | Total GEN active power | Pgen | 1530-1531 | S32 | 4 |  | W | [5 empty] | X | √ | X | X
总GEN无功功率 | Total GEN reactive power | Qgen | 1532-1533 | S32 | 4 |  | Var |  |  |  | 新增单位Var | Add new unit Var | X | √ | X | X
总GEN视在功率 | Total GEN apparent power | Sgen | 1534-1535 | U32 | 4 |  | VA |  |  |  | 新增单位VA | Add new unit VA | X | √ | X | X
当日GEN发电量 | GEN power generation on that day | EgenDay | 1536 | U16 | 2 |  | 0.1kwh |  |  |  | 新增单位0.1kwh | New unit 0.1kwh | X | √ | X | X
总EPS放电量 | Total EPS discharge | EepsInvTotal | 1537-1538 | U32 | 4 |  | 0.1kwh | [5 empty] | X | √ | X | X
总EPS充电量 | Total EPS charging capacity | EepsRecTotal | 1539-1540 | U32 | 4 |  | 0.1kwh | [5 empty] | X | √ | X | X
总GEN发电量 | Total GEN power generation | EgenTotal | 1541-1542 | U32 | 4 |  | 0.1kwh | [5 empty] | X | √ | X | X
预留 | reserved | Reserve | 1543-1999 | [9 empty] | X | √ | X | X
实时运行信息4（电池运行信息） | [12 empty] | X | √ | X | X
电池状态 | battery status | BatState | 2000 | U16 | 2 |  |  | 无电池 故障 休眠 起动 运行充电 运行放电 运行停止 | No battery Fault hibernate start Run charging Running discharge Operation stopped |  | 不包括强充 | Excludes forced charging | X | √ | X | X
电池温度 | battery temperature | Tbat | 2001 | s16 | 2 |  | 0.1℃ | [5 empty] | X | √ | X | X
电池电量（SOC） | Battery power (SOC) | SOC | 2002 | U16 | 2 |  | % | [5 empty] | X | √ | X | X
电池健康状况(SOH) | Battery State of Health (SOH) | SOH | 2003 | U16 | 2 |  | % | [5 empty] | X | √ | X | X
电池电压 | battery voltage | Vbat | 2004 | U16 | 2 |  | 0.1V | [5 empty] | X | √ | X | X
电池电流 | battery current | Ibat | 2005 | S16 | 2 |  | 0.01A | 正表示电池充电 负表示电池放电 | Positive means the battery is charging Negative means the battery is discharged |  |  |  | X | √ | X | X
BuckBoost电压 | BuckBoost voltage | Vbb | 2006 | U16 | 2 |  | 0.1V | [5 empty] | X | √ | X | X
电池总功率 | total battery power | Pbat | 2007-2008 | S32 | 4 |  | 1W | 正表示电池充电 负表示电池放电 | Positive means the battery is charging Negative means the battery is discharged |  | 1.改为有符号数, 2. 单位0.1V修改为1W | 1. Change to signed number, 2. Unit 0.1V changed to 1W | X | √ | X | X
电池当日充电量 | Battery charge capacity for the day | EChgDay | 2009 | U16 | 2 |  | 0.1kwh |  |  | 存 | 单位0.1wh修改为0.1kwh | Unit 0.1wh changed to 0.1kwh | X | √ | X | X
电池当日放电量 | Battery discharge capacity on the day | EDischgDay | 2010 | U16 | 2 |  | 0.1kwh |  |  | 存 |  |  | X | √ | X | X
总电池充电量 | Total battery charge | EChgTotal | 2011-2012 | U32 | 4 |  | 0.1kwh |  |  |  | 新增单位0.1kwh | New unit 0.1kwh | X | √ | X | X
总电池放电量 | Total battery discharge | EDischgTotal | 2013-2014 | U32 | 4 |  | 0.1kwh |  |  |  | 新增单位0.1kwh | New unit 0.1kwh | X | √ | X | X
电池控制命令 | battery control command | BatCtrlCmd | 2015 | U16 | 2 |  |  | bit0-1: 0-无操作,1-高压上电,2-高压下电 bit2:充电 bit3:放电 bit4:重启 bit5:关机 bit6-15:保留 | bit0-1: 0-no operation, 1-high voltage power on, 2-high voltage power off bit2: charging bit3: discharge bit4:restart bit5: shutdown bit6-15: reserved |  |  |  | X | √ | X | X
电池连接状态 | Battery connection status | StorConn | 2016 | U16 | 2 | B0:CONNECTED B1:AVAILABLE B2:OPERATING B3:TEST | [6 empty] | X | √ | X | X
预留 | reserved | Reserve | 2017-2499 | [9 empty] | X | √ | X | X
实时运行信息5(系统信息) | [8 empty] | Real-time operation information 5 (system information) |  |  |  | X | √ | X | X
运行状态 | Running status | RunState | 2500 | U16 | 2 |  |  | 初始上电0 待机1 起动2 运行并网3 运行离网4 运行柴发5 并网切离网6 离网切并网7 掉电处理8 关机9 故障10 升级11 老化12 开环13 采样校准14 | Initial power-on 0 Standby 1 Start 2 Run grid connection 3 Running Off Grid 4 Running diesel engine 5 On-grid and off-grid 6 Off-grid and on-grid connection 7 Power outage handling 8 shutdown 9 Fault 10 Upgrade 11 Aging 12 Open loop 13 Sampling calibration 14 |  |  |  | X | √ | X | X
当前触发限功率方式 | Current trigger power limiting mode | PLimitMode | 2501-2502 | U32 | 4 |  |  | 0x0000 无限功率 0x0001 温度限功率 0x0002 手动设置限功率 0x0004 电网电压兼PF限功率 0x0008 过频限功率 0x0010 单独PV2输入限功率 0x0020 故障恢复缓启限功率 0x0040 预留通道 | 0x0000 unlimited power 0x0001 Temperature limit power 0x0002 Manually set power limit 0x0004 Grid voltage and PF power limit 0x0008 Over frequency power limit 0x0010 Individual PV2 input power limit 0x0020 Fault recovery slow start power limit 0x0040 reserved channel |  | 具体的限功率方式可以再添加，建议留U32。 | Specific power limiting methods can be added, but it is recommended to leave U32. | X | √ | X | X
当前触发电网调度模式 | Current triggering grid dispatch mode | GridCrlMode | 2503-2504 | U32 | 4 |  |  | 0 E_GRID_ADJUST_DEF 1 E_GRID_ADJUST_LVRT 2 E_GRID_ADJUST_FIXE, 3 E_GRID_ADJUST_PF 4 E_GRID_ADJUST_QP 5 E_GRID_ADJUST_TEST | 0 E_GRID_ADJUST_DEF 1E_GRID_ADJUST_LVRT 2 E_GRID_ADJUST_FIXE, 3E_GRID_ADJUST_PF 4E_GRID_ADJUST_QP 5 E_GRID_ADJUST_TEST |  | 应该按位呈现，可能几种组合同时出现，建议留U32。 | It should be presented bit by bit, and several combinations may appear at the same time. It is recommended to leave U32. | X | √ | X | X
PV1的MPPT工作模式 | MPPT working mode of PV1 | PV1MpptMode | 2505 | U16 | 2 |  |  | 0 缺省值 1 待机 2 Boost扫描 3 Bus扫描 4 Boost MPPT运行 5 Bus MPPT运行 6 集中Bus运行 | 0 default value 1 standby 2 Boost scan 3 Bus scan 4 Boost MPPT operation 5 Bus MPPT operation 6 Centralized Bus operation |  |  |  | X | √ | X | X
PV2的MPPT工作模式 | MPPT working mode of PV2 | PV2MpptMode | 2506 | U16 | 2 | [7 empty] | X | √ | X | X
PV3的MPPT工作模式 | MPPT working mode of PV3 | PV3MpptMode | 2507 | U16 | 2 | [7 empty] | X | √ | X | X
PV4的MPPT工作模式 | MPPT working mode of PV4 | PV4MpptMode | 2508 | U16 | 2 | [7 empty] | X | √ | X | X
PV5的MPPT工作模式 | MPPT working mode of PV5 | PV5MpptMode | 2509 | U16 | 2 | [7 empty] | X | √ | X | X
PV6的MPPT工作模式 | MPPT working mode of PV6 | PV6MpptMode | 2510 | U16 | 2 | [7 empty] | X | √ | X | X
可调负载DO状态 | Adjustable load DO status | LoadCtrlState | 2511 | U16 | 2 | [7 empty] | X | √ | X | X
电表主动检测状态 | Electric meter actively detects status | MeterTestState | 2512 | U16 | 2 | [7 empty] | X | √ | X | X
起动时间 | Start time | ConncetTime | 2513 | U16 | 2 |  | S | [5 empty] | X | √ | X | X
逆变器内部温度 | Inverter internal temperature | Tinner | 2514 | S16 | 2 |  | 0.1℃ | [5 empty] | X | √ | X | X
变压器温度 | Transformer temperature | Ttransf | 2515 | S16 | 2 |  | 0.1℃ | [5 empty] | X | √ | X | X
温度1 | Temperature 1 | Temp1 | 2516 | S16 | 2 |  | 0.1℃ | [5 empty] | X | √ | X | X
温度2 | Temperature 2 | Temp2 | 2517 | S16 | 2 |  | 0.1℃ | [5 empty] | X | √ | X | X
调试信息1 | Debug information 1 | DebugInfo1 | 2518 | U16 | 2 | [7 empty] | X | √ | X | X
调试信息2 | Debug information 2 | DebugInfo2 | 2519 | U16 | 2 | [7 empty] | X | √ | X | X
调试信息3 | Debug information 3 | DebugInfo3 | 2520 | U16 | 2 | [7 empty] | X | √ | X | X
调试信息4 | Debug information 4 | DebugInfo4 | 2521 | U16 | 2 | [7 empty] | X | √ | X | X
调试信息5 | Debug information 5 | DebugInfo5 | 2522 | U16 | 2 | [7 empty] | X | √ | X | X
调试信息6 | Debug information 6 | DebugInfo6 | 2523 | U16 | 2 | [7 empty] | X | √ | X | X
预留 | reserved | Reserve | 2524-2999 | [9 empty] | X | √ | X | X
实时运行信息6（故障及告警） | [8 empty] | Real-time operating information 6 (faults and alarms) |  |  |  | X | √ | X | X
PV故障1 | PV failure 1 | PvErr1 | 3000-3001 | U32 | 4 | [7 empty] | X | √ | X | X
PV故障2 | PV failure 2 | PvErr2 | 3002-3003 | U32 | 4 | [7 empty] | X | √ | X | X
电池故障1 | Battery failure 1 | BatErr1 | 3004-3005 | U32 | 4 | [7 empty] | X | √ | X | X
电池故障2 | Battery failure 2 | BatErr2 | 3006-3007 | U32 | 4 | [7 empty] | X | √ | X | X
电网故障 | Grid failure | GridErr | 3008-3009 | U32 | 4 | [7 empty] | X | √ | X | X
离网故障 | Off-grid failure | OffGridErr | 3010-3011 | U32 | 4 | [7 empty] | X | √ | X | X
直流侧故障1 | DC side fault 1 | DCErr1 | 3012-3013 | U32 | 4 | [7 empty] | X | √ | X | X
直流侧故障2 | DC side fault 2 | DCErr2 | 3014-3015 | U32 | 4 | [7 empty] | X | √ | X | X
交流侧故障 | AC side fault | ACErr | 3016-3017 | U32 | 4 | [7 empty] | X | √ | X | X
系统故障1 | System failure 1 | SysErr1 | 3018-3019 | U32 | 4 | [7 empty] | X | √ | X | X
系统故障2 | System failure 2 | SysErr2 | 3020-3021 | U32 | 4 | [7 empty] | X | √ | X | X
永久故障 | permanent failure | PermErr | 3022-3023 | U32 | 4 | [7 empty] | X | √ | X | X
内部告警 | Internal alarm | InWarning | 3024-3025 | U32 | 4 | [7 empty] | X | √ | X | X
外部告警 | external alarm | OutWarning | 3026-3027 | U32 | 4 | [7 empty] | X | √ | X | X
预留 | reserved | Reserve | 3028-3499 | [9 empty] | X | √ | X | X

## 参数读写03-06-10-Parameter reading
name | Translation | English | address | data type | Number of bytes | data range |  | unit | Remark |  | Whether to store to external flash |  | Revise |  | variable name
名称 | Translation | 英文 | 地址 | 数据类型 | 字节数 | 数据范围 | Translation | 单位 | 备注 |  | 是否存储到外部flash | Translation | 修改 | Translation | 变量名称 | 0x03 | 0x04 | 0x06 | 0x10
设置参数1（系统参数）Setting parameters 1 (system parameters) | [15 empty] | 功能码 Function code
额定有功功率 | Rated active power | NormActPower | 200-201 | U32 | 4 |  |  | W |  | #VALUE! |  |  |  |  | gulDeNormActPwr | √ | X | √ | √
额定视在功率 | Rated apparent power | NormAppPower | 202-203 | U32 | 4 |  |  | VA | [6 empty] | gulDeNormAppPwr | √ | X | √ | √
国家选择 | Country selection | Country | 204 | U16 | 2 | 国家 | nation |  | 设置好需要重启逆变器 | After setting, you need to restart the inverter. | 是 | yes |  |  | guwDeSafty | √ | X | √ | √
PV输入模式 | PV input mode | PVInputType | 205 | U16 | 2 |  |  |  | 0:独立 1:并联 2:无PV | 0: independent 1: Parallel connection 2: No PV | 是 | yes | 新增 2:无PV | Added 2: No PV | guwDePvInputType | √ | X | √ | √
运行功能使能 | Run function enable | FuncEn | 206-207 | U32 | 4 |  |  |  | B0:开关机 B1:Soft start enable B2:Power soft B3:EPS Mode enable B4:Timing AC charge enable B5:Timing charge enable B6:Timing discharge enable B7:JET simulating test B8:DRMS enable B9:ripple control B10:电网高压降载 B11:电网低压升载 B12:电网过频降载 B13:电网欠频升载 B14:HVRT B15:LVRT B16:Timing Forbid discharge enable B17~B31 Reseved | B0: On/off machine B1:Soft start enable B2:Power soft B3:EPS Mode enable B4:Timing AC charge enable B5:Timing charge enable B6:Timing discharge enable B7:JET simulating test B8:DRMS enable B9:ripple control B10: Grid high voltage load reduction B11: Grid low voltage load boosting B12: Grid overfrequency and load reduction B13: Grid underfrequency and load increase B14:HVRT B15:LVRT B16:Timing Forbid discharge enable B17~B31 Reseved | 是 | yes | 1. B5与B6调换位置，修改B16为Forbid discharge enable，移除B17。 2. “AC charge enable”修改为“Timing AC charge enable” “Forced charge enable”修改为“Timing charge enable” “Forced discharge enable”修改为“Timing discharge enable” “Forbid discharge enable”修改为“Timing Forbid discharge enable” | 1. Change the positions of B5 and B6, modify B16 to Forbid discharge enable, and remove B17. 2. Change "AC charge enable" to "Timing AC charge enable" "Forced charge enable" is changed to "Timing charge enable" "Forced discharge enable" is changed to "Timing discharge enable" "Forbid discharge enable" is changed to "Timing Forbid discharge enable" | gulDeSysFuncEn | √ | X | √ | √
保护功能使能 | Protection function enabled | ProtectEn | 208-209 | U32 | 4 |  |  |  | B0:并网范围判断 B1:AactiveIsland; B2:PassiveIsland; B3:OverVolt; B4:UnderVolt; B5:OverFreq; B6:UnderFreq; B7:10minOverVolt; B8:IsoChk; B9:DciChk; B10:GfciChk; B11:EarthChk; B12:三相不平衡; B13:电网暂态电压保护; B14:Bus中点不平衡保护; B15:PV反接; B16:PV异常; B17:采样检测; B18:温度采样异常; B19:高低温保护; B20:GEN电压频率检测; B21:继电器检测; B22:内部通信检测; B23:风扇检测; B24:电表&CT检测 B25~B31 Reseved | B0: Judgment of grid connection range B1:AactiveIsland; B2:PassiveIsland; B3:OverVolt; B4:UnderVolt; B5:OverFreq; B6:UnderFreq; B7:10minOverVolt; B8:IsoChk; B9:DciChk; B10:GfciChk; B11:EarthChk; B12: Three-phase unbalance; B13: Grid transient voltage protection; B14: Bus midpoint imbalance protection; B15: PV reverse connection; B16: Abnormal PV; B17: Sampling and testing; B18: Abnormal temperature sampling; B19: High and low temperature protection; B20: GEN voltage frequency detection; B21: Relay detection; B22: Internal communication detection; B23: Fan detection; B24: Electric meter & CT detection B25~B31 Reseved | 是 | yes |  |  | gulDeSysProtectEn | √ | X | √ | √
PV启动电压 | PV starting voltage | PvStartVolt | 210 | U16 | 2 |  |  | 0.1V |  |  | 是 | yes |  |  | guwDeStartVpv | √ | X | √ | √
CT or Meter | CT or Meter | MeterType | 211 | U16 | 2 | 0：no merter 1：CT 2：meter |  |  |  |  | 是 | yes |  |  | guwDeMeterType | √ | X | √ | √
电表厂家 | Meter manufacturer | MeterBrand | 212 | U16 | 2 | 1： 2： |  |  |  |  | 是 | yes |  |  | guwDeMeterBrand | √ | X | √ | √
CT系数 | CT coefficient | CTRatio | 213 | U16 | 2 | [5 empty] | 是 | yes |  |  |  | √ | X | √ | √
LoadMinLoad | LoadMinLoad | MinLoad | 214-215 | S32 | 4 |  |  | W | 用于负载均衡功能，负载小时从电网取电 | Used for load balancing function, taking power from the grid during load hours |  | #VALUE! |  |  |  | √ | X | √ | √
PV扫描模式 | PV scan mode | PvScanModel | 216 | U16 | 2 | 0: 关闭 1: 开一次 2: 周期定时 3: 绝对时间定时 | 0: off 1: Open once 2: Periodic timing 3: Absolute time timing |  |  |  |  | #VALUE! |  |  | guwDePvScanModel | √ | X | √ | √
PV扫描周期 | PV scan cycle | PvScanPrd | 217 | U16 | 2 | [6 empty] | #VALUE! |  |  | guwDePvScanPrd | √ | X | √ | √
PV扫描时间1 | PV scan time 1 | PvScanTime1 | 218 | U16 | 2 | [6 empty] | #VALUE! |  |  | guwDePvScanT1 | √ | X | √ | √
PV扫描时间2 | PV scan time 2 | PvScanTime2 | 219 | U16 | 2 | [6 empty] | #VALUE! |  |  | guwDePvScanT2 | √ | X | √ | √
PV扫描时间3 | PV scan time 3 | PvScanTime3 | 220 | U16 | 2 | [6 empty] | #VALUE! |  |  | guwDePvScanT3 | √ | X | √ | √
最大交流输出电流 | Maximum AC output current | MaxAcOutCurr | 221-222 | U32 | 4 |  |  | 0.01A |  |  | 是 | yes |  |  | guwDeMaxAcOutCurr | √ | X | √ | √
预留 | reserved | Reserve | 223-499 | [8 empty] | #VALUE! |  |  |  | √ | X | √ | √
设置参数2（系统指令） | Set parameter 2 (system command) | [10 empty] | #VALUE! |  |  |  | √ | X | √ | √
时间 | time | TimeYear-Month | 500 | U16 | 2 | H:18-99 L:1-12 |  |  |  |  | 否 | no |  |  | guwDeSysTYearMonth | √ | X | √ | √
| #VALUE! | TimeDate-Hour | 501 | U16 | 2 | H:1-31 L:0-23 |  |  |  |  | 否 | no |  |  | guwDeSysTDateHour | √ | X | √ | √
| #VALUE! | TimeMinute-Sec | 502 | U16 | 2 | H:0-59 L:0-59 |  |  |  |  | 否 | no |  |  | guwDeSysTMinuteSec | √ | X | √ | √
采集器IP地址和SN | Collector IP address and SN | IP15-14 | 503 | U16 | 2 | ASCII |  |  |  |  | 否 | no |  |  | guwDeGprsIP7 | √ | X | √ | √
| #VALUE! | IP13-12 | 504 | U16 | 2 | ASCII |  |  |  |  | 否 | no |  |  | guwDeGprsIP6 | √ | X | √ | √
| #VALUE! | IP11-10 | 505 | U16 | 2 | ASCII |  |  |  |  | 否 | no |  |  | guwDeGprsIP5 | √ | X | √ | √
| #VALUE! | IP9-8 | 506 | U16 | 2 | ASCII |  |  |  |  | 否 | no |  |  | guwDeGprsIP4 | √ | X | √ | √
| #VALUE! | IP7-6 | 507 | U16 | 2 | ASCII |  |  |  |  | 否 | no |  |  | guwDeGprsIP3 | √ | X | √ | √
| #VALUE! | IP5-4 | 508 | U16 | 2 | ASCII |  |  |  |  | 否 | no |  |  | guwDeGprsIP2 | √ | X | √ | √
| #VALUE! | IP3-2 | 509 | U16 | 2 | ASCII |  |  |  |  | 否 | no |  |  | guwDeGprsIP1 | √ | X | √ | √
| #VALUE! | IP1-0 | 510 | U16 | 2 | ASCII |  |  |  |  | 否 | no |  |  | guwDeGprsIP0 | √ | X | √ | √
| #VALUE! | SerialNumber15-14 | 511 | U16 | 2 | ASCII |  |  |  |  | 否 | no |  |  | guwDeGprsSN7 | √ | X | √ | √
| #VALUE! | SerialNumber13-12 | 512 | U16 | 2 | ASCII |  |  |  |  | 否 | no |  |  | guwDeGprsSN6 | √ | X | √ | √
| #VALUE! | SerialNumber11-10 | 513 | U16 | 2 | ASCII |  |  |  |  | 否 | no |  |  | guwDeGprsSN5 | √ | X | √ | √
| #VALUE! | SerialNumber9-8 | 514 | U16 | 2 | ASCII |  |  |  |  | 否 | no |  |  | guwDeGprsSN4 | √ | X | √ | √
| #VALUE! | SerialNumber7-6 | 515 | U16 | 2 | ASCII |  |  |  |  | 否 | no |  |  | guwDeGprsSN3 | √ | X | √ | √
| #VALUE! | SerialNumber5-4 | 516 | U16 | 2 | ASCII |  |  |  |  | 否 | no |  |  | guwDeGprsSN2 | √ | X | √ | √
| #VALUE! | SerialNumber3-2 | 517 | U16 | 2 | ASCII |  |  |  |  | 否 | no |  |  | guwDeGprsSN1 | √ | X | √ | √
| #VALUE! | SerialNumber1-0 | 518 | U16 | 2 | ASCII |  |  |  |  | 否 | no |  |  | guwDeGprsSN0 | √ | X | √ | √
允许写操作密码 | Allow write operation password | WrPassWord | 519-520 | U32 | 4 | ASCII |  |  | 通讯密码 只有当密码通过是才可以进行写操作 只需要ARM操作 | Communication password can only be written when the password is passed. Only ARM operation is required. | 否 | no |  |  | gulDeWriteKey | √ | X | X | X
升级使能 | Upgrade enabled | UpdataEn | 521 | U16 | 2 |  |  |  | 0xAA有效 | 0xAA is valid | 否 | no |  |  | guwDeUpdataEn | √ | X | X | √
升级波特率 | Upgrade baud rate | UpdataBaud | 522 | U16 | 2 |  |  |  | 0: 9600 1: 115200 | 0: 9600 1: 115200 | 否 | no |  |  | guwDeUpdataBaud | √ | X | X | √
升级哪个程序 | Which program to upgrade | UpdataCpuNum | 523 | U16 | 2 |  |  |  | 1：HMI(显示板) 2: Master(主DSP) 3: Slave(副DSP) | 1: HMI (display panel) 2: Master (main DSP) 3: Slave(Slave DSP) | 否 | no |  |  | guwDeUpdataCpuNum | √ | X | X | √
| #VALUE! | UpdataPackSize(升级程序包大小) | 524 | U16 | 2 | [5 empty] | 否 | no |  |  | guwDeUpdataPackSize | √ | X | X | √
开始故障录波密码 | Password to start fault recording | StartErrWaveKey | 525 | U16 | 2 | [5 empty] | 否 | no |  |  | guwDeFaultWaveKey | √ | X | √ | √
读取故障录波信息 | Read fault recording information | ReadErrWave | 526 | U16 | 2 |  |  |  | 0xAA:最近一条 0x55:全部故障 | 0xAA: latest one 0x55: all faults | 否 | no |  |  | guwDeFaultWaveRead | √ | X | √ | √
功能执行指令 | Function execution instructions | FuncCmd | 527-528 | U32 | 4 | B0-B2: 0闭环，1老化，2校准，3开环，4单板调试 B3: 强制复位 B4: 恢复出厂 B5: 清除记录信息 B6: 恢复默认参数 B7: 永久故障恢复 B8: 电表主动检测指令 B9: 风扇启动 B10: 负载开关 | B0-B2: 0 closed loop, 1 aging, 2 calibration, 3 open loop, 4 single board debugging B3: Forced reset B4: Factory reset B5: Clear record information B6: Restore default parameters B7: Permanent failure recovery B8: Meter active detection command B9: Fan starts B10: Load switch |  |  |  |  | #VALUE! |  |  | gulDeSysFuncCmd | √ | X | √ | √
调试参数通道1 | Debugging parameter channel 1 | DebugPara1 | 529 | U16 | 2 | [5 empty] | 否 | no |  |  | guwDeDebugPara1 | √ | X | √ | √
调试参数通道2 | Debug parameter channel 2 | DebugPara2 | 530 | U16 | 2 | [5 empty] | 否 | no |  |  | guwDeDebugPara2 | √ | X | √ | √
调试参数通道3 | Debug parameter channel 3 | DebugPara3 | 531 | U16 | 2 | [5 empty] | 否 | no |  |  | guwDeDebugPara3 | √ | X | √ | √
调试参数通道4 | Debug parameter channel 4 | DebugPara4 | 532 | U16 | 2 | [5 empty] | 否 | no |  |  | guwDeDebugPara4 | √ | X | √ | √
调试参数通道5 | Debug parameter channel 5 | DebugPara5 | 533 | U16 | 2 | [5 empty] | 否 | no |  |  | guwDeDebugPara5 | √ | X | √ | √
调试参数通道6 | Debug parameter channel 6 | DebugPara6 | 534 | U16 | 2 | [5 empty] | 否 | no |  |  | guwDeDebugPara6 | √ | X | √ | √
预留 | reserved | Reserve | 535-999 |  | 930 | [6 empty] | #VALUE! |  |  |  | √ | X | √ | √
设置参数3（保护参数） | Set parameter 3 (protection parameters) | [10 empty] | #VALUE! |  |  |  | √ | X | √ | √
并网条件判断时间 | Grid connection condition judgment time | GridOnJudgTime | 1000 | U16 | 2 | 10-1200 |  | S |  |  | 是 | yes |  |  | guwDeGridOnJudgT | √ | X | √ | √
并网允许最大电压 | Maximum voltage allowed for grid connection | GridOnVoltMax | 1001 | U16 | 2 | 1010-3200 |  | 0.1V |  |  | 是 | yes |  |  | guwDeGridOnVMax | √ | X | √ | √
并网允许最小电压 | Minimum voltage allowed for grid connection | GridOnVoltMin | 1002 | U16 | 2 | 500-2300 |  | 0.1V |  |  | 是 | yes |  |  | guwDeGridOnVMin | √ | X | √ | √
并网允许最大频率 | Maximum frequency allowed for grid connection | GridOnFreqMax | 1003 | U16 | 2 | 5000-7000 |  | 0.01Hz |  |  | 是 | yes |  |  | guwDeGridOnFMax | √ | X | √ | √
并网允许最小频率 | Minimum frequency allowed for grid connection | GridOnFreqMin | 1004 | U16 | 2 | 4000-6000 |  |  |  |  | 是 | yes |  |  | guwDeGridOnFMin | √ | X | √ | √
电压保护几级级跳脱选择 | Voltage protection level trip selection | VoltProtectStage | 1005 | U16 | 2 | 1-5 |  |  | 1:1级 默认1级 2: 2级 3: 3级 4: 4级 5: 5级 | 1: Level 1 Default level 1 2: Level 2 3: Level 3 4: Level 4 5: Level 5 | 是 | yes |  |  | guwDeVoltProtectStage | √ | X | √ | √
频率保护几级级跳脱选择 | Frequency protection level trip selection | FreqProtectStage | 1006 | U16 | 2 | 1-5 |  |  | 1:1级 默认1级 2: 2级 3: 3级 4: 4级 5: 5级 | 1: Level 1 Default level 1 2: Level 2 3: Level 3 4: Level 4 5: Level 5 | 是 | yes |  |  | guwDeFreqProtectStage | √ | X | √ | √
电网过压恢复点 | Grid overvoltage recovery point | GridVoltMaxRecover | 1007 | U16 | 2 | 1010-3200 |  | 0.1V |  |  | 是 | yes |  |  | guwDeGridVMaxRec | √ | X | √ | √
电网欠压恢复点 | Grid undervoltage recovery point | GridVoltMinRecover | 1008 | U16 | 2 | 500-2300 |  | 0.1V |  |  | 是 | yes |  |  | guwDeGridVMinRec | √ | X | √ | √
电网过频恢复点 | Grid overfrequency recovery point | GridFreqMaxRecover | 1009 | U16 | 2 | 5000-7000 |  | 0.01Hz |  |  | 是 | yes |  |  | guwDeGridFMaxRec | √ | X | √ | √
电网欠频恢复点 | Grid underfrequency recovery point | GridFreqMinRecover | 1010 | U16 | 2 | 4000-6000 |  | 0.01Hz |  |  | 是 | yes |  |  | guwDeGridFMinRec | √ | X | √ | √
电网过压一级保护值 （默认单级） | Grid overvoltage level one protection value (default single level) | GridVoltMax1 | 1011 | U16 | 2 | 1000-4000 |  | 0.1V |  |  | 是 | yes |  |  | guwDeGridVMax1 | √ | X | √ | √
电网过压一级保护时间 （默认单级） | Grid overvoltage level one protection time (default single level) | GridVoltMaxTime1 | 1012 | U16 | 2 | 0-30000(所有保护) | 0-30000 (all protections) | 0.01S |  |  | 是 | yes |  |  | guwDeGridVMaxTime1 | √ | X | √ | √
电网欠压一级保护值 （默认单级） | Grid undervoltage first-level protection value (default single level) | GridVoltMin1 | 1013 | U16 | 2 | 500-2500 | 500-2500 | 0.1V |  |  | 是 | yes |  |  | guwDeGridVMin1 | √ | X | √ | √
电网欠压一级保护时间 （默认单级） | Grid undervoltage first-level protection time (default single level) | GridVoltMinTime1 | 1014 | U16 | 2 | 0-30000(所有保护) | 0-30000 (all protections) | 0.01S |  |  | 是 | yes |  |  | guwDeGridVMinTime1 | √ | X | √ | √
电网过压二级保护值 | Grid overvoltage secondary protection value | GridVoltMax2 | 1015 | U16 | 2 | 1000-4000 | 1000-4000 | 0.1V |  |  | 是 | yes |  |  | guwDeGridVMax2 | √ | X | √ | √
电网过压二级保护时间 | Grid overvoltage secondary protection time | GridVoltMaxTime2 | 1016 | U16 | 2 | 0-30000(所有保护) | 0-30000 (all protections) | 0.01S |  |  | 是 | yes |  |  | guwDeGridVMaxTime2 | √ | X | √ | √
电网欠压二级保护值 | Grid undervoltage secondary protection value | GridVoltMin2 | 1017 | U16 | 2 | 500-2500 | 500-2500 | 0.1V |  |  | 是 | yes |  |  | guwDeGridVMin2 | √ | X | √ | √
电网欠压二级保护时间 | Grid undervoltage secondary protection time | GridVoltMinTime2 | 1018 | U16 | 2 | 0-30000(所有保护) | 0-30000 (all protections) | 0.01S |  |  | 是 | yes |  |  | guwDeGridVMinTime2 | √ | X | √ | √
电网过压三级保护值 | Grid overvoltage level three protection value | GridVoltMax3 | 1019 | U16 | 2 | 1000-4000 | 1000-4000 | 0.1V |  |  | 是 | yes |  |  | guwDeGridVMax3 | √ | X | √ | √
电网过压三级保护时间 | Grid overvoltage level three protection time | GridVoltMaxTime3 | 1020 | U16 | 2 | 0-30000(所有保护) | 0-30000 (all protections) | 0.01S |  |  | 是 | yes |  |  | guwDeGridVMaxTime3 | √ | X | √ | √
电网欠压三级保护值 | Grid undervoltage three-level protection value | GridVoltMin3 | 1021 | U16 | 2 | 500-2500 | 500-2500 | 0.1V |  |  | 是 | yes |  |  | guwDeGridVMin3 | √ | X | √ | √
电网欠压三级保护时间 | Grid undervoltage level 3 protection time | GridVoltMinTime3 | 1022 | U16 | 2 | 0-30000(所有保护) | 0-30000 (all protections) | 0.01S |  |  | 是 | yes |  |  | guwDeGridVMinTime3 | √ | X | √ | √
电网过压四级保护值 | Grid overvoltage level four protection value | GridVoltMax4 | 1023 | U16 | 2 | 1000-4000 | 1000-4000 | 0.1V |  |  | 是 | yes |  |  | guwDeGridVMax4 | √ | X | √ | √
电网过压四级保护时间 | Grid overvoltage level 4 protection time | GridVoltMaxTime4 | 1024 | U16 | 2 | 0-30000(所有保护) | 0-30000 (all protections) | 0.01S |  |  | 是 | yes |  |  | guwDeGridVMaxTime4 | √ | X | √ | √
电网欠压四级保护值 | Grid undervoltage level four protection value | GridVoltMin4 | 1025 | U16 | 2 | 500-2500 | 500-2500 | 0.1V |  |  | 是 | yes |  |  | guwDeGridVMin4 | √ | X | √ | √
电网欠压四级保护时间 | Grid undervoltage level 4 protection time | GridVoltMinTime4 | 1026 | U16 | 2 | 0-30000(所有保护) | 0-30000 (all protections) | 0.01S |  |  | 是 | yes |  |  | guwDeGridVMinTime4 | √ | X | √ | √
电网过压五级保护值 | Grid overvoltage five-level protection value | GridVoltMax5 | 1027 | U16 | 2 | 1000-4000 | 1000-4000 | 0.1V |  |  | 是 | yes |  |  | guwDeGridVMax5 | √ | X | √ | √
电网过压五级保护时间 | Grid overvoltage level five protection time | GridVoltMaxTime5 | 1028 | U16 | 2 | 0-30000(所有保护) | 0-30000 (all protections) | 0.01S |  |  | 是 | yes |  |  | guwDeGridVMaxTime5 | √ | X | √ | √
电网欠压五级保护值 | Grid undervoltage five-level protection value | GridVoltMin5 | 1029 | U16 | 2 | 500-2500 | 500-2500 | 0.1V |  |  | 是 | yes |  |  | guwDeGridVMin5 | √ | X | √ | √
电网欠压五级保护时间 | Grid undervoltage level 5 protection time | GridVoltMinTime5 | 1030 | U16 | 2 | 0-30000(所有保护) | 0-30000 (all protections) | 0.01S |  |  | 是 | yes |  |  | guwDeGridVMinTime5 | √ | X | √ | √
电网过频一级保护值 （默认单级） | Grid overfrequency first-level protection value (default single level) | GridFreqMax1 | 1031 | U16 | 2 | 5000-7000 | 5000-7000 | 0.01Hz |  |  | 是 | yes |  |  | guwDeGridFMax1 | √ | X | √ | √
电网过频一级保护时间 （默认单级） | Grid overfrequency first-level protection time (default single level) | GridFreqMaxTime1 | 1032 | U16 | 2 | 0-30000(所有保护) | 0-30000 (all protections) | 0.01S |  |  | 是 | yes |  |  | guwDeGridFMaxTime1 | √ | X | √ | √
电网欠频一级保护值 （默认单级） | Grid underfrequency first-level protection value (default single level) | GridFreqMin1 | 1033 | U16 | 2 | 4000-6000 | 4000-6000 | 0.01Hz |  |  | 是 | yes |  |  | guwDeGridFMin1 | √ | X | √ | √
电网欠频一级保护时间 （默认单级） | Grid underfrequency first-level protection time (default single level) | GridFreqMinTime1 | 1034 | U16 | 2 | 0-30000(所有保护) | 0-30000 (all protections) | 0.01S |  |  | 是 | yes |  |  | guwDeGridFMinTime1 | √ | X | √ | √
电网过频二级保护值 | Grid overfrequency secondary protection value | GridFreqMax2 | 1035 | U16 | 2 | 5000-7000 | 5000-7000 | 0.01Hz |  |  | 是 | yes |  |  | guwDeGridFMax2 | √ | X | √ | √
电网过频二级保护时间 | Grid overfrequency secondary protection time | GridFreqMaxTime2 | 1036 | U16 | 2 | 0-30000(所有保护) | 0-30000 (all protections) | 0.01S |  |  | 是 | yes |  |  | guwDeGridFMaxTime2 | √ | X | √ | √
电网欠频二级保护值 | Grid underfrequency secondary protection value | GridFreqMin2 | 1037 | U16 | 2 | 4000-6000 | 4000-6000 | 0.01Hz |  |  | 是 | yes |  |  | guwDeGridFMin2 | √ | X | √ | √
电网欠频二级保护时间 | Grid underfrequency secondary protection time | GridFreqMinTime2 | 1038 | U16 | 2 | 0-30000(所有保护) | 0-30000 (all protections) | 0.01S |  |  | 是 | yes |  |  | guwDeGridFMinTime2 | √ | X | √ | √
电网过频三级保护值 | Grid overfrequency three-level protection value | GridFreqMax3 | 1039 | U16 | 2 | 5000-7000 | 5000-7000 | 0.01Hz |  |  | 是 | yes |  |  | guwDeGridFMax3 | √ | X | √ | √
电网过频三级保护时间 | Grid overfrequency level three protection time | GridFreqMaxTime3 | 1040 | U16 | 2 | 0-30000(所有保护) | 0-30000 (all protections) | 0.01S |  |  | 是 | yes |  |  | guwDeGridFMaxTime3 | √ | X | √ | √
电网欠频三级保护值 | Grid underfrequency three-level protection value | GridFreqMin3 | 1041 | U16 | 2 | 4000-6000 | 4000-6000 | 0.01Hz |  |  | 是 | yes |  |  | guwDeGridFMin3 | √ | X | √ | √
电网欠频三级保护时间 | Grid underfrequency level three protection time | GridFreqMinTime3 | 1042 | U16 | 2 | 0-30000(所有保护) | 0-30000 (all protections) | 0.01S |  |  | 是 | yes |  |  | guwDeGridFMinTime3 | √ | X | √ | √
电网过频四级保护值 | Grid overfrequency four-level protection value | GridFreqMax4 | 1043 | U16 | 2 | 5000-7000 |  | 0.01Hz |  |  | 是 | yes |  |  | guwDeGridFMax4 | √ | X | √ | √
电网过频四级保护时间 | Grid overfrequency level 4 protection time | GridFreqMaxTime4 | 1044 | U16 | 2 | 0-30000 |  | 0.01S |  |  | 是 | yes |  |  | guwDeGridFMaxTime4 | √ | X | √ | √
电网欠频四级保护值 | Grid underfrequency level four protection value | GridFreqMin4 | 1045 | U16 | 2 | 4000-6000 |  | 0.01Hz |  |  | 是 | yes |  |  | guwDeGridFMin4 | √ | X | √ | √
电网欠频四级保护时间 | Grid underfrequency level 4 protection time | GridFreqMinTime4 | 1046 | U16 | 2 | 0-30000 |  | 0.01S |  |  | 是 | yes |  |  | guwDeGridFMinTime4 | √ | X | √ | √
电网过频五级保护值 | Five-level protection value for power grid overfrequency | GridFreqMax5 | 1047 | U16 | 2 | 5000-7000 |  | 0.01Hz |  |  | 是 | yes |  |  | guwDeGridFMax5 | √ | X | √ | √
电网过频五级保护时间 | Grid overfrequency five-level protection time | GridFreqMaxTime5 | 1048 | U16 | 2 | 0-30000 |  | 0.01S |  |  | 是 | yes |  |  | guwDeGridFMaxTime5 | √ | X | √ | √
电网欠频五级保护值 | Power grid underfrequency five-level protection value | GridFreqMin5 | 1049 | U16 | 2 | 4000-6000 |  | 0.01Hz |  |  | 是 | yes |  |  | guwDeGridFMin5 | √ | X | √ | √
电网欠频五级保护时间 | Grid underfrequency level five protection time | GridFreqMinTime5 | 1050 | U16 | 2 | 0-30000 |  | 0.01S |  |  | 是 | yes |  |  | guwDeGridFMinTime5 | √ | X | √ | √
10分钟平均电压保护值 | 10-minute average voltage protection value | 10minGridVoltMax | 1051 | U16 | 2 | 1000-4000 |  | 0.1V |  |  | 是 | yes |  |  | guwDe10minGridVMax | √ | X | √ | √
10分钟平均电压恢复值 | 10-minute average voltage recovery value | 10minGridVoltMaxRecover | 1052 | U16 | 2 | 1000-4000 |  | 0.1V |  |  | 是 | yes |  |  | guwDe10minGridVMaxRec | √ | X | √ | √
绝缘阻抗下限 | Insulation resistance lower limit | IsoResMin | 1053 | U16 | 2 | 10-800 |  | KΩ |  |  | 是 | yes |  |  | guwDeIsoResMin | √ | X | √ | √
直流分量上限 | DC component upper limit | DcIMax | 1054 | U16 | 2 | 20-2000 |  | mA |  |  | 是 | yes |  |  | guwDeDcIMax | √ | X | √ | √
持续漏电流保护值 | Continuous leakage current protection value | ContLeakMax | 1055 | U16 | 2 | 20-2000 |  | mA |  |  |  | #VALUE! |  |  | guwDeContLeakMax | √ | X | √ | √
持续漏电流保护时间 | Continuous leakage current protection time | ContLeakMaxTime | 1056 | U16 | 2 | 0-30000 |  | 0.01S |  |  |  | #VALUE! |  |  | guwDeContLeakMaxTime | √ | X | √ | √
突变漏电流保护值 | Sudden leakage current protection value | SuddenLeakMax | 1057 | U16 | 2 | 20-2000 |  | mA |  |  |  | #VALUE! |  |  | guwDeSuddenLeakMax | √ | X | √ | √
突变漏电流保护时间 | Sudden leakage current protection time | SuddenLeakMaxTime | 1058 | U16 | 2 | 0-30000 |  | 0.01S |  |  |  | #VALUE! |  |  | guwDeSuddenLeakMaxTime | √ | X | √ | √
三相不平衡度 | Three-phase unbalance | GridVoltUnbalMax | 1059 | U16 | 2 | 70-100 |  | % |  |  | 是 | yes |  |  | guwDeGridVoltUnbalMax | √ | X | √ | √
三相不平衡保护时间 | Three-phase unbalance protection time | GridVoltUnbalMaxTime | 1060 | U16 | 2 | [6 empty] | #VALUE! |  |  | guwDeGridVoltUnbalMaxTime | √ | X | √ | √
环境温度上限 | upper limit of ambient temperature | AmbiTempMax | 1061 | S16 | 2 | 25-100 |  | ℃ |  |  | 是 | yes |  |  | gwDeAmbiTempMax | √ | X | √ | √
环境温度下限 | Ambient temperature lower limit | AmbiTempMin | 1062 | S16 | 2 | -40-25 |  | ℃ |  |  |  | #VALUE! |  |  | gwDeAmbiTempMin | √ | X | √ | √
模块温度上限 | Module temperature upper limit | ModulTempMax | 1063 | S16 | 2 | 85-200 |  | ℃ |  |  | 是 | yes |  |  | gwDeModulTempMax | √ | X | √ | √
暂态电压保护值 | Transient voltage protection value | GridVoltFastMax | 1064 | U16 | 2 | 101-320V*1.414 |  | 0.1V |  |  | 是 | yes |  |  | guwDeGridVFastMax | √ | X | √ | √
暂态电压保护时间 | Transient voltage protection time | GridVoltFastMaxTime | 1065 | U16 | 2 | 1-10中断周期 |  |  |  |  | 是 | yes |  |  | guwDeGridVFastMaxTime | √ | X | √ | √
BUS中点不平衡保护值 | BUS midpoint unbalance protection value | BusMidDifMax | 1066 | U16 | 2 | 30-1000 |  | 0.1V |  |  | 是 | yes |  |  | guwDeBusMidDifMax | √ | X | √ | √
离网电压直流分量保护值 | Off-grid voltage DC component protection value | DcVMax | 1067 | U16 | 2 | 20-5000 |  | 0.001V |  |  |  | #VALUE! |  |  |  | √ | X | √ | √
预留 | reserved | Reserve | 1067-1499 | [8 empty] | #VALUE! |  |  |  | √ | X | √ | √
设置参数4（电网调度参数1） | Set parameter 4 (grid dispatch parameter 1) | [10 empty] | #VALUE! |  |  |  | √ | X | √ | √
无功阈值 | Reactive power threshold | NormReactPower | 1500-1501 | U32 | 4 | 0-200000 |  | VA |  |  | 是 | yes |  |  | glDeNormReactPwr | √ | X | √ | √
有功输出限制 | Active output limit | OutPwrMaxPer | 1502 | U16 | 2 | 0-1000 |  | 0.1% |  |  | 是 | yes |  |  | guwDeOutPwrMaxPer | √ | X | √ | √
最大有功输出功率 | Maximum active output power | OutPwrMax | 1503-1504 | U32 | 4 | 0-200000 |  | W |  |  | 是 | yes |  |  | gulDeOutPwrMax | √ | X | √ | √
过频降额曲线 | Overfrequency derating curve | PbyFOverCurve | 1505 | U16 | 2 | [5 empty] | 是 | yes |  |  | guwDePbyFOverCurve | √ | X | √ | √
过频降额F1 | Over frequency derating F1 | PbyFOverF1 | 1506 | U16 | 2 | 5000-7000 |  | 0.01Hz |  |  | 是 | yes |  |  | guwDePbyFOverF1 | √ | X | √ | √
过频降额F2 | Over frequency derating F2 | PbyFOverF2 | 1507 | U16 | 2 | 5000-7000 |  | 0.01Hz |  |  | 是 | yes |  |  | guwDePbyFOverF2 | √ | X | √ | √
过频降额F3 | Overfrequency derating F3 | PbyFOverF3 | 1508 | U16 | 2 | 5000-7000 |  | 0.01Hz |  |  | 是 | yes |  |  | guwDePbyFOverF3 | √ | X | √ | √
过频降额F4 | Over frequency derating F4 | PbyFOverF4 | 1509 | U16 | 2 | 5000-7000 |  | 0.01Hz |  |  | 是 | yes |  |  | guwDePbyFOverF4 | √ | X | √ | √
过频降额P1 | Over frequency derating P1 | PbyFOverP1 | 1510 | S16 | 2 | 0-2000 |  | 0.1% |  |  | 是 | yes |  |  | gwDePbyFOverP1 | √ | X | √ | √
过频降额P2 | Overfrequency derating P2 | PbyFOverP2 | 1511 | S16 | 2 | 0-2000 |  | 0.1% |  |  | 是 | yes |  |  | gwDePbyFOverP2 | √ | X | √ | √
过频降额P3 | Over frequency derating P3 | PbyFOverP3 | 1512 | S16 | 2 | 0-2000 |  | 0.1% |  |  | 是 | yes |  |  | gwDePbyFOverP3 | √ | X | √ | √
过频降额P4 | Over frequency derating P4 | PbyFOverP4 | 1513 | S16 | 2 | 0-2000 |  | 0.1% |  |  | 是 | yes |  |  | gwDePbyFOverP4 | √ | X | √ | √
过频降额恢复点 | Overfrequency derating recovery point | PbyFOverFRecover | 1514 | U16 | 2 | 5000-7000 |  | 0.01Hz |  |  | 是 | yes |  |  | guwDePbyFOverFRecover | √ | X | √ | √
过频降额时有功降额速率 | Active power derating rate during over-frequency derating | PbyFOverRate | 1515 | U16 | 2 | 0-5000 |  | 0.1%/Hz |  |  | 是 | yes |  |  | guwDePbyFOverRate | √ | X | √ | √
过频降额后等待恢复时间 | Waiting time for recovery after overfrequency derating | PbyFOverTRecover | 1516 | U16 | 2 | [5 empty] | 是 | yes |  |  | guwDePbyFOverTRecover | √ | X | √ | √
过频降额后有功恢复速率 | Active power recovery rate after over-frequency derating | PbyFOverRateRecover | 1517 | U16 | 2 | [5 empty] | 是 | yes |  |  | guwDePbyFOverRateRecover | √ | X | √ | √
过频降额响应时间 | Overfrequency derating response time | PbyFOverT | 1518 | U16 | 2 | [5 empty] | 是 | yes |  |  | guwDePbyFOverT | √ | X | √ | √
欠频升额曲线 | Underfrequency escalation curve | PbyFRiseCurve | 1519 | U16 | 2 | [5 empty] | 是 | yes |  |  | guwDePbyFRiseCurve | √ | X | √ | √
欠频升额F1 | Underfrequency increase F1 | PbyFRiseF1 | 1520 | U16 | 2 | 4000-6000 |  | 0.01Hz |  |  | 是 | yes |  |  | guwDePbyFRiseF1 | √ | X | √ | √
欠频升额F2 | Underfrequency increase F2 | PbyFRiseF2 | 1521 | U16 | 2 | 4000-6000 |  | 0.01Hz |  |  | 是 | yes |  |  | guwDePbyFRiseF2 | √ | X | √ | √
欠频升额F3 | Underfrequency increase F3 | PbyFRiseF3 | 1522 | U16 | 2 | 4000-6000 |  | 0.01Hz |  |  | 是 | yes |  |  | guwDePbyFRiseF3 | √ | X | √ | √
欠频升额F4 | Underfrequency increase F4 | PbyFRiseF4 | 1523 | U16 | 2 | 4000-6000 |  | 0.01Hz |  |  | 是 | yes |  |  | guwDePbyFRiseF4 | √ | X | √ | √
欠频升额P1 | Underfrequency increase P1 | PbyFRiseP1 | 1524 | S16 | 2 | 0-2000 |  | 0.1% |  |  | 是 | yes |  |  | gwDePbyFRiseP1 | √ | X | √ | √
欠频升额P2 | Underfrequency increase P2 | PbyFRiseP2 | 1525 | S16 | 2 | 0-2000 |  | 0.1% |  |  | 是 | yes |  |  | gwDePbyFRiseP2 | √ | X | √ | √
欠频升额P3 | Underfrequency increase to P3 | PbyFRiseP3 | 1526 | S16 | 2 | 0-2000 |  | 0.1% |  |  | 是 | yes |  |  | gwDePbyFRiseP3 | √ | X | √ | √
欠频升额P4 | Underfrequency increase to P4 | PbyFRiseP4 | 1527 | S16 | 2 | 0-2000 |  | 0.1% |  |  | 是 | yes |  |  | gwDePbyFRiseP4 | √ | X | √ | √
欠频升额恢复点 | Underfrequency increase recovery point | PbyFRiseFRecover | 1528 | U16 | 2 | 4000-6000 |  | 0.01Hz |  |  | 是 | yes |  |  | guwDePbyFRiseFRecover | √ | X | √ | √
欠频升额时有功升额速率 | Active power increase rate during under frequency increase | PbyFRiseRate | 1529 | U16 | 2 | 0-5000 |  | 0.1%/Hz |  |  | 是 | yes |  |  | guwDePbyFRiseRate | √ | X | √ | √
欠频升额后等待恢复时间 | Wait for recovery time after under-frequency increase | PbyFRiseTRecover | 1530 | U16 | 2 | [5 empty] | 是 | yes |  |  | guwDePbyFRiseTRecover | √ | X | √ | √
欠频升额后有功恢复速率 | Active power recovery rate after underfrequency increase | PbyFRiseRateRecover | 1531 | U16 | 2 | [5 empty] | 是 | yes |  |  | guwDePbyFRiseRateRecover | √ | X | √ | √
欠频升额响应时间 | Under frequency increase response time | PbyFRiseT | 1532 | U16 | 2 | [5 empty] | 是 | yes |  |  | guwDePbyFRiseT | √ | X | √ | √
电网过压功率调节电压1 | Grid overvoltage power regulation voltage 1 | PbyVOverV1 | 1533 | U16 | 2 | 1000-4000 |  | 0.1V |  |  | 是 | yes |  |  | guwDePbyVOverV1 | √ | X | √ | √
电网过压功率调节电压2 | Grid overvoltage power regulation voltage 2 | PbyVOverV2 | 1534 | U16 | 2 | 1000-4000 |  | 0.1V |  |  | 是 | yes |  |  | guwDePbyVOverV2 | √ | X | √ | √
电网过压功率调节电压3 | Grid overvoltage power regulation voltage 3 | PbyVOverV3 | 1535 | U16 | 2 | 1000-4000 |  | 0.1V |  |  | 是 | yes |  |  | guwDePbyVOverV3 | √ | X | √ | √
电网过压功率调节电压4 | Grid overvoltage power regulation voltage 4 | PbyVOverV4 | 1536 | U16 | 2 | 1000-4000 |  | 0.1V |  |  | 是 | yes |  |  | guwDePbyVOverV4 | √ | X | √ | √
电网过压功率调节功率1 | Grid overvoltage power regulation power 1 | PbyVOverP1 | 1537 | S16 | 2 | 0-2000 |  | 0.1% |  |  | 是 | yes |  |  | gwDePbyVOverP1 | √ | X | √ | √
电网过压功率调节功率2 | Grid overvoltage power regulation power 2 | PbyVOverP2 | 1538 | S16 | 2 | 0-2000 |  | 0.1% |  |  | 是 | yes |  |  | gwDePbyVOverP2 | √ | X | √ | √
电网过压功率调节功率3 | Grid overvoltage power regulation power 3 | PbyVOverP3 | 1539 | S16 | 2 | 0-2000 |  | 0.1% |  |  | 是 | yes |  |  | gwDePbyVOverP3 | √ | X | √ | √
电网过压功率调节功率4 | Grid overvoltage power regulation power 4 | PbyVOverP4 | 1540 | S16 | 2 | 0-2000 |  | 0.1% |  |  | 是 | yes |  |  | gwDePbyVOverP4 | √ | X | √ | √
电网过压功率调节时间 | Grid overvoltage power adjustment time | PbyVOverT | 1541 | U16 | 2 | 0-30000 |  | 0.01s |  |  | 是 | yes |  |  | guwDePbyVOverT | √ | X | √ | √
电网欠压功率调节电压1 | Grid undervoltage power regulation voltage 1 | PbyVUnderV1 | 1542 | U16 | 2 | 500-2500 |  | 0.1V |  |  | 是 | yes |  |  | guwDePbyVUnderV1 | √ | X | √ | √
电网欠压功率调节电压2 | Grid undervoltage power regulation voltage 2 | PbyVUnderV2 | 1543 | U16 | 2 | 500-2500 |  | 0.1V |  |  | 是 | yes |  |  | guwDePbyVUnderV2 | √ | X | √ | √
电网欠压功率调节电压3 | Grid undervoltage power regulation voltage 3 | PbyVUnderV3 | 1544 | U16 | 2 | 500-2500 |  | 0.1V |  |  | 是 | yes |  |  | guwDePbyVUnderV3 | √ | X | √ | √
电网欠压功率调节电压4 | Grid undervoltage power regulation voltage 4 | PbyVUnderV4 | 1545 | U16 | 2 | 500-2500 |  | 0.1V |  |  | 是 | yes |  |  | guwDePbyVUnderV4 | √ | X | √ | √
电网欠压功率调节功率1 | Grid undervoltage power regulation power 1 | PbyVUnderP1 | 1546 | S16 | 2 | 0-2000 |  | 0.1% |  |  | 是 | yes |  |  | gwDePbyVUnderP1 | √ | X | √ | √
电网欠压功率调节功率2 | Grid undervoltage power regulation power 2 | PbyVUnderP2 | 1547 | S16 | 2 | 0-2000 |  | 0.1% |  |  | 是 | yes |  |  | gwDePbyVUnderP2 | √ | X | √ | √
电网欠压功率调节功率3 | Grid undervoltage power regulation power 3 | PbyVUnderP3 | 1548 | S16 | 2 | 0-2000 |  | 0.1% |  |  | 是 | yes |  |  | gwDePbyVUnderP3 | √ | X | √ | √
电网欠压功率调节功率4 | Grid undervoltage power adjustment power 4 | PbyVUnderP4 | 1549 | S16 | 2 | 0-2000 |  | 0.1% |  |  | 是 | yes |  |  | gwDePbyVUnderP4 | √ | X | √ | √
电网欠压功率调节时间 | Grid undervoltage power adjustment time | PbyVUnderT | 1550 | U16 | 2 | 0-30000 |  | 0.01s |  |  | 是 | yes |  |  | guwDePbyVUnderT | √ | X | √ | √
无功控制 | Reactive power control | QMode | 1551 | U16 | 2 |  |  |  | 0：Normal 1：Q Set(配合P1518) 2：Pf Set(配合P1519) 3：Q By V(配合P1520~1525) 4：Pf By P(配合P1526~1527) | 0：Normal 1: Q Set (with P1518) 2: Pf Set (with P1519) 3: Q By V (with P1520~1525) 4: Pf By P (with P1526~1527) | 是 | yes |  |  | guwDeQMode | √ | X | √ | √
无功功率设置% | Reactive power setting % | QSet% | 1552 | S16 | 2 | (-1000~1000) |  | 0.001 |  |  |  | #VALUE! |  |  | gwDeQPerSet | √ | X | √ | √
无功功率设置 | Reactive power settings | QSet | 1553-1554 | S32 | 4 | ‘-200000~200000 |  | VA |  |  | 是 | yes |  |  | glDeQSet | √ | X | √ | √
功率因数设置 | Power factor setting | PfSet | 1555 | S16 | 2 | (-1000~-800,800~1000) |  | 0.001 | V1<V2<V3<V4 |  | 是 | yes |  |  | gwDePfSet | √ | X | √ | √
QByV_V1 | QByV_V1 | QByVV1 | 1556 | U16 | 2 | 800-1000 |  | 0.1% |  |  |  | #VALUE! |  |  | guwDeQByVV1 | √ | X | √ | √
QByV_V2 | QByV_V2 | QByVV2 | 1557 | U16 | 2 | 800-1000 |  | 0.1% |  |  |  | #VALUE! |  |  | guwDeQByVV2 | √ | X | √ | √
QByV_V3 | QByV_V3 | QByVV3 | 1558 | U16 | 2 | 1000-1100 |  | 0.1% |  |  |  | #VALUE! |  |  | guwDeQByVV3 | √ | X | √ | √
QByV_V4 | QByV_V4 | QByVV4 | 1559 | U16 | 2 | 1000-1200 |  | 0.1% |  |  |  | #VALUE! |  |  | guwDeQByVV4 | √ | X | √ | √
QByV_Pct1 | QByV_Pct1 | QByVQ1 | 1560 | S16 | 2 | 0-40 |  | 0.1% |  |  | 是 | yes |  |  | gwDeQByVQ1 | √ | X | √ | √
QByV_Pct2 | QByV_Pct2 | QByVQ2 | 1561 | S16 | 2 | [6 empty] | #VALUE! |  |  | gwDeQByVQ2 | √ | X | √ | √
QByV_Pct3 | QByV_Pct3 | QByVQ3 | 1562 | S16 | 2 | [6 empty] | #VALUE! |  |  | gwDeQByVQ3 | √ | X | √ | √
QByV_Pct4 | QByV_Pct4 | QByVQ4 | 1563 | S16 | 2 | -40-0 |  | 0.1% |  |  | 是 | yes |  |  | gwDeQByVQ4 | √ | X | √ | √
PfByPPStart | PfByPPStart | PfByPPStart | 1564 | S16 | 2 | 40-100 |  | 0.1% |  |  | 是 | yes |  |  | gwDePfByPPStart | √ | X | √ | √
PfByPPfEnd | PfByPPfEnd | PfByPPfEnd | 1565 | S16 | 2 | (-1000~-800,800~1000) |  | 0.001 |  |  | 是 | yes |  |  | gwDePfByPPfEnd | √ | X | √ | √
PfByPRate | PfByPRate | PfByPRate | 1566 | U16 | 2 | 0-5000 |  | 0.1%Hz |  |  |  | #VALUE! |  |  | guwDePfByPRate | √ | X | √ | √
PfByP_P1 | PfByP_P1 | PfByPP1 | 1567 | S16 | 2 | -1000-+1000 |  | 0.1% |  |  |  | #VALUE! |  |  | gwDePfByPP1 | √ | X | √ | √
PfByP_P2 | PfByP_P2 | PfByPP2 | 1568 | S16 | 2 | -1000-+1000 |  | 0.1% |  |  |  | #VALUE! |  |  | gwDePfByPP2 | √ | X | √ | √
PfByP_P3 | PfByP_P3 | PfByPP3 | 1569 | S16 | 2 | -1000-+1000 |  | 0.1% |  |  |  | #VALUE! |  |  | gwDePfByPP3 | √ | X | √ | √
PfByP_P4 | PfByP_P4 | PfByPP4 | 1570 | S16 | 2 | -1000-+1000 |  | 0.1% |  |  |  | #VALUE! |  |  | gwDePfByPP4 | √ | X | √ | √
PfByP_Pf1 | PfByP_Pf1 | PfByPPf1 | 1571 | S16 | 2 | -100--1000, +100-+1000 |  | 0.1% |  |  |  | #VALUE! |  |  | gwDePfByPPf1 | √ | X | √ | √
PfByP_Pf2 | PfByP_Pf2 | PfByPPf2 | 1572 | S16 | 2 | -100--1000, +100-+1000 |  | 0.1% |  |  |  | #VALUE! |  |  | gwDePfByPPf2 | √ | X | √ | √
PfByP_Pf3 | PfByP_Pf3 | PfByPPf3 | 1573 | S16 | 2 | -100--1000, +100-+1000 |  | 0.1% |  |  |  | #VALUE! |  |  | gwDePfByPPf3 | √ | X | √ | √
PfByP_Pf4 | PfByP_Pf4 | PfByPPf4 | 1574 | S16 | 2 | -100--1000, +100-+1000 |  | 0.1% |  |  |  | #VALUE! |  |  | gwDePfByPPf4 | √ | X | √ | √
Q(P)功能使能的电压比例点 | Voltage proportional point when Q(P) function is enabled | PfByPEnV | 1575 | U16 | 2 | [5 empty] | 是 | yes |  |  | guwDePfByPEnV | √ | X | √ | √
Q(P)功能退出使能的电压比例点 | Q(P) function exit enable voltage proportional point | PfByPDisV | 1576 | U16 | 2 | [5 empty] | 是 | yes |  |  | guwDePfByPDisV | √ | X | √ | √
Q(P)功能退出使能的功率比例点 | Q(P) function exit enable power proportional point | PfByPDisP | 1577 | S16 | 2 | [5 empty] | 是 | yes |  |  | gwDePfByPDisP | √ | X | √ | √
Q(U)功能使能的功率比例点 | Power proportional point when Q(U) function is enabled | QByVEnP | 1578 | S16 | 2 | [5 empty] | 是 | yes |  |  | gwDeQByVEnP | √ | X | √ | √
Q(U)功能退出使能的功率比例点 | Q(U) function exit enable power proportional point | QByVDisP | 1579 | S16 | 2 | [5 empty] | 是 | yes |  |  | gwDeQByVDisP | √ | X | √ | √
有功无功控制使能 | Active and reactive power control enable | PwrCtrlEn | 1580 | U16 | 2 |  |  |  | (只对Sunspec要求的设定值起作用) B0:有功设定限制使能 B1:PF设定控制使能 B2:无功设定控制使能 B3:无功volt_var曲线使能 B4:有功freq_watt曲线使能 B5:有功曲线滞环使能(对外0代表使能) B6:无功watt_pf曲线使能 B7:有功volt_watt曲线使能 B8:并网使能(connect) | (Only affects the setting values ​​required by Sunspec) B0: Active power setting limit enable B1: PF setting control enable B2: Reactive power setting control enable B3: Reactive power volt_var curve enable B4: Active power freq_watt curve enable B5: Enable active power curve hysteresis (external 0 means enable) B6: Reactive power watt_pf curve enable B7: Active power volt_watt curve enable B8: Grid connection enable (connect) | 是 | yes | 修改并新增B3、B4、B5、 B6 、B7 、B8 | Modify and add B3, B4, B5, B6, B7, B8 | guwDePwrCtrlEn | √ | X | √ | √
无功基值选择 | Reactive power base value selection | VarDeptRef | 1581 | U16 | 2 |  |  |  | 1：WMax 2：VArMax 3：VArAval |  | 是 | yes |  |  | guwDeVarDeptRef | √ | X | √ | √
有功基值选择 | Active base value selection | WDeptRef | 1582 | U16 | 2 |  |  |  | 1：WMax 2：WAval |  |  | #VALUE! |  |  | guwDeWDeptRef | √ | X | √ | √
预留 | reserved | Reserve | 1583-1999 | [8 empty] | #VALUE! |  |  |  | √ | X | √ | √
设置参数5（电网调度参数2） | Set parameter 5 (grid dispatch parameter 2) | [10 empty] | #VALUE! |  |  |  | √ | X | √ | √
LVRT保护级数 | LVRT protection level | LvrtStage | 2000 | U16 | 2 | 1--5 |  |  | 2 |  | 是 | yes |  |  | guwDeLvrtStage | √ | X | √ | √
LVRT电网不平衡支撑开关 | LVRT grid unbalance support switch | LvrtUnbalSuppEn | 2001 | U16 | 2 |  |  |  | 0xAA |  | 是 | yes |  |  | guwDeLvrtUnbalSuppEn | √ | X | √ | √
LVRT零功率模式 | LVRT zero power mode | Lvrt0PEn | 2002 | U16 | 2 |  |  |  | 0xAA |  | 是 | yes |  |  | guwDeLvrt0PEn | √ | X | √ | √
LVRT K因数 | LVRT K factor | LvrtK | 2003 | U16 | 2 |  |  |  | 0 |  | 是 | yes |  |  | guwDeLvrtK | √ | X | √ | √
LVRT无功功率指令 | LVRT reactive power directive | LvrtQ | 2004 | S16 | 2 | -1000-+1000 |  | 0.1% |  |  |  | #VALUE! |  |  | gwDeLvrtQ | √ | X | √ | √
LVRT有功恢复时间 | LVRT active power recovery time | LvrtPRecT | 2005 | U16 | 2 | 0-30000 |  | 0.01s |  |  |  | #VALUE! |  |  | guwDeLvrtPRecT | √ | X | √ | √
LVRT电压1 | LVRT voltage 1 | LvrtV1 | 2006 | U16 | 2 | 0-2500 |  | 0.1V | 1840 |  | 是 | yes |  |  | guwDeLvrtV1 | √ | X | √ | √
LVRT电压2 | LVRT voltage 2 | LvrtV2 | 2007 | U16 | 2 | 0-2500 |  | 0.1V | 345（1110） |  | 是 | yes |  |  | guwDeLvrtV2 | √ | X | √ | √
LVRT电压3 | LVRT voltage 3 | LvrtV3 | 2008 | U16 | 2 | 0-2500 |  | 0.1V | 305 |  | 是 | yes |  |  | guwDeLvrtV3 | √ | X | √ | √
LVRT电压4 | LVRT voltage 4 | LvrtV4 | 2009 | U16 | 2 | 0-2500 |  | 0.1V | 305 |  | 是 | yes |  |  | guwDeLvrtV4 | √ | X | √ | √
LVRT电压5 | LVRT voltage 5 | LvrtV5 | 2010 | U16 | 2 | 0-2500 |  | 0.1V | 305 |  | 是 | yes |  |  | guwDeLvrtV5 | √ | X | √ | √
LVRT时间1 | LVRT time 1 | LvrtT1 | 2011 | U16 | 2 | 0-30000 |  | 0.01s | 3050 |  | 是 | yes |  |  | guwDeLvrtT1 | √ | X | √ | √
LVRT时间2 | LVRT time 2 | LvrtT2 | 2012 | U16 | 2 | 0-30000 |  | 0.01s | 3050 |  | 是 | yes |  |  | guwDeLvrtT2 | √ | X | √ | √
LVRT时间3 | LVRT time 3 | LvrtT3 | 2013 | U16 | 2 | 0-30000 |  | 0.01s | 200 |  | 是 | yes |  |  | guwDeLvrtT3 | √ | X | √ | √
LVRT时间4 | LVRT time 4 | LvrtT4 | 2014 | U16 | 2 | 0-30000 |  | 0.01s | 200 |  | 是 | yes |  |  | guwDeLvrtT4 | √ | X | √ | √
LVRT时间5 | LVRT time 5 | LvrtT5 | 2015 | U16 | 2 | 0-30000 |  | 0.01s | 200 |  | 是 | yes |  |  | guwDeLvrtT5 | √ | X | √ | √
HVRT保护级数 | HVRT protection level | HvrtStage | 2016 | U16 | 2 | 1--5 |  |  | 2 |  | 是 | yes |  |  | guwDeHvrtStage | √ | X | √ | √
HVRT电网不平衡支撑开关 | HVRT grid unbalance support switch | HvrtUnbalSuppEn | 2017 | U16 | 2 |  |  |  | 0xAA |  | 是 | yes |  |  | guwDeHvrtUnbalSuppEn | √ | X | √ | √
HVRT零功率模式 | HVRT zero power mode | Hvrt0PEn | 2018 | U16 | 2 |  |  |  | 0xAA |  | 是 | yes |  |  | guwDeHvrt0PEn | √ | X | √ | √
HVRT K因数 | HVRT K-factor | HvrtK | 2019 | U16 | 2 |  |  |  | 0 |  | 是 | yes |  |  | guwDeHvrtK | √ | X | √ | √
HVRT无功功率指令 | HVRT reactive power directive | HvrtQ | 2020 | S16 | 2 | -1000-+1000 |  | 0.001 |  |  |  | #VALUE! |  |  | gwDeHvrtQ | √ | X | √ | √
HVRT有功恢复时间 | HVRT active power recovery time | HvrtPRecT | 2021 | U16 | 2 | 0-30000 |  | 0.01s |  |  |  | #VALUE! |  |  | guwDeHvrtPRecT | √ | X | √ | √
HVRT电压1 | HVRT voltage 1 | HvrtV1 | 2022 | U16 | 2 | 1000-4000 |  | 0.1V | 2645 |  | 是 | yes |  |  | guwDeHvrtV1 | √ | X | √ | √
HVRT电压2 | HVRT voltage 2 | HvrtV2 | 2023 | U16 | 2 | 1000-4000 |  | 0.1V | 2760（2800） |  | 是 | yes |  |  | guwDeHvrtV2 | √ | X | √ | √
HVRT电压3 | HVRT voltage 3 | HvrtV3 | 2024 | U16 | 2 | 1000-4000 |  | 0.1V | 2915 |  | 是 | yes |  |  | guwDeHvrtV3 | √ | X | √ | √
HVRT电压4 | HVRT voltage 4 | HvrtV4 | 2025 | U16 | 2 | 1000-4000 |  | 0.1V | 2915 |  | 是 | yes |  |  | guwDeHvrtV4 | √ | X | √ | √
HVRT电压5 | HVRT voltage 5 | HvrtV5 | 2026 | U16 | 2 | 1000-4000 |  | 0.1V | 2915 |  | 是 | yes |  |  | guwDeHvrtV5 | √ | X | √ | √
HVRT时间1 | HVRT time 1 | HvrtT1 | 2027 | U16 | 2 | 0-30000 |  | 0.01s | 5050 |  | 是 | yes |  |  | guwDeHvrtT1 | √ | X | √ | √
HVRT时间2 | HVRT time 2 | HvrtT2 | 2028 | U16 | 2 | 0-30000 |  | 0.01s | 100 |  | 是 | yes |  |  | guwDeHvrtT2 | √ | X | √ | √
HVRT时间3 | HVRT time 3 | HvrtT3 | 2029 | U16 | 2 | 0-30000 |  | 0.01s | 100 |  | 是 | yes |  |  | guwDeHvrtT3 | √ | X | √ | √
HVRT时间4 | HVRT time 4 | HvrtT4 | 2030 | U16 | 2 | 0-30000 |  | 0.01s | 100 |  | 是 | yes |  |  | guwDeHvrtT4 | √ | X | √ | √
HVRT时间5 | HVRT time 5 | HvrtT5 | 2031 | U16 | 2 | 0-30000 |  | 0.01s | 100 |  | 是 | yes |  |  | guwDeHvrtT5 | √ | X | √ | √
DRM模式 | DRM mode | DRMModel | 2032 | U16 | 2 | 1~9：DRM0~8 ; 其他值无效 | 1~9: DRM0~8; other values ​​are invalid |  |  |  | 是 | yes |  |  | guwDeDRMModel | √ | X | √ | √
DRM限功率值 | DRM power limit value | DRMPLimit | 2033 | S16 | 2 | [5 empty] | 是 | yes |  |  | gwDeDRMPLimit | √ | X | √ | √
DRM PF值 | DRM PF value | DRMPFSet | 2034 | S16 | 2 | [5 empty] | 是 | yes |  |  | gwDeDRMPFSet | √ | X | √ | √
RIPPLE CONTROL模式 | RIPPLE CONTROL MODE | RCModel | 2035 | U16 | 2 | 1~5：RIPP0~4 ; 其他值无效（包括0） | 1~5: RIPP0~4; other values ​​are invalid (including 0) |  |  |  | 是 | yes |  |  | guwDeRCModel | √ | X | √ | √
RIPPLE CONTROL输出限功率 | RIPPLE CONTROL output power limit | RCPLimit | 2036 | S16 | 2 | 0~1000 |  |  |  |  | 是 | yes |  |  | gwDeRCPLimit | √ | X | √ | √
初始连网时间 | Initial connection time | IniConnecT | 2037 | U16 | 2 | [6 empty] | #VALUE! |  |  | guwDeIniConnecT | √ | X | √ | √
故障重连时间 | Failure reconnection time | ReConnecT | 2038 | U16 | 2 | 20-600 |  | S |  |  | 是 | yes |  |  | guwDeReConnecT | √ | X | √ | √
馈网限功率值 | Feeder network power limit value | GridFeedPlimit | 2039-2040 | S32 | 4 | 0-1000 |  | 0.1% |  |  | 是 | yes |  |  | glDeGridFeedPlimit | √ | X | √ | √
电网取电限功率值 | Power grid power limit value | GridBackPlimit | 2041-2042 | S32 | 4 | [6 empty] | #VALUE! |  |  | glDeGridBackPlimit | √ | X | √ | √
软起斜率 | soft slope | SoftStartSlope | 2043 | U16 | 2 | 0-100 |  | % | 并网软起斜率 | Grid-connected soft starting slope | 是 | yes |  |  | guwDeSoftStartSlope | √ | X | √ | √
功率缓变上升斜率 | Power ramp up slope | SoftIncSlope | 2044 | U16 | 2 | [6 empty] | #VALUE! |  |  | guwDeSoftIncSlope | √ | X | √ | √
功率缓变下降斜率 | Power ramp down slope | SoftDecSlope | 2045 | U16 | 2 | [6 empty] | #VALUE! |  |  | guwDeSoftDecSlope | √ | X | √ | √
预留 | reserved | Reserve | 2046-2499 | [8 empty] | #VALUE! |  |  |  | √ | X | √ | √
设置参数6（EMS） | Set parameter 6 (EMS) | [10 empty] | #VALUE! |  |  |  | √ | X | √ | √
EMS模式 | EMS mode | EMSMode | 2500 | U16 | 2 |  |  |  | 0:SelfUse 1:CharFst 2:SellFst 3:Maintain 4:CmdChar 5:ExtEms |  | 是 | yes |  |  | guwDeEMSMode | √ | X | √ | √
充放电指令 | Charge and discharge instructions | ChgCmd | 2501 | U16 | 2 | 0xAA:充放电 0xBB:停止 0xCC:充电 0xDD:放电 | 0xAA: charge and discharge 0xBB: Stop 0xCC: charging 0xDD: discharge |  |  |  | 否 | no |  |  | guwDeChgCmd | √ | X | √ | √
充放电功率指令 | Charge and discharge power instructions | ChgPowerSet | 2502-2503 | S32 | 4 | [5 empty] | 否 | no | “充放电功率”修改为“充放电功率指令” | "Charge and discharge power" is changed to "charge and discharge power command" | glDeChgPowerSet | √ | X | √ | √
AC充电功率百分比 | AC charging power percentage | AcPChgMax | 2504 | U16 | 2 | 0-100 |  | % |  |  | 是 | yes |  |  | guwDeCurrMaxAcChg | √ | X | √ | √
AC充电最大SOC | AC charging maximum SOC | AcSocMaxChg | 2505 | U16 | 2 | 0-100 |  | % |  |  | 是 | yes | “最大充电SOC”修改为“AC充电最大SOC”；“SocMaxChg”修改为“AcSocMaxChg” | "Maximum charging SOC" is modified to "AC charging maximum SOC"; "SocMaxChg" is modified to "AcSocMaxChg" | guwDeSocMaxChg | √ | X | √ | √
强制放电最小SOC | Forced discharge minimum SOC | SocMaxDisChg | 2506 | U16 | 2 | 0-100 |  | % |  |  | 是 | yes | “最小放电SOC”修改为“强制放电最小SOC”； | "Minimum discharge SOC" is changed to "forced discharge minimum SOC"; | guwDeSocMaxDisChg | √ | X | √ | √
强制充电功率百分比 | Forced charging power percentage | PChgMax | 2507 | U16 | 2 | 0-100 |  | % |  |  | 是 | yes |  |  | guwDePChgMax | √ | X | √ | √
强制放电功率百分比 | Forced discharge power percentage | PDisChgMax | 2508 | U16 | 2 | 0-100 |  | % |  |  | 是 | yes |  |  | guwDePDisChgMax | √ | X | √ | √
AC充电开始时间1 | AC charging start time 1 | TimeOnAcChg1 | 2509 | U16 | 2 | H:0-23 M:0-59 |  |  | 结合实际项目区分周末和工作日 | Distinguish between weekends and working days based on actual projects | 是 | yes |  |  | guwDeTimeOnAcChg1 | √ | X | √ | √
AC充电结束时间1 | AC charging end time 1 | TimeOffAcChg1 | 2510 | U16 | 2 | H:0-23 M:0-59 |  |  |  |  | 是 | yes |  |  | guwDeTimeOffAcChg1 | √ | X | √ | √
AC充电开始时间2 | AC charging start time 2 | TimeOnAcChg2 | 2511 | U16 | 2 | H:0-23 M:0-59 |  |  |  |  | 是 | yes |  |  | guwDeTimeOnAcChg2 | √ | X | √ | √
AC充电结束时间2 | AC charging end time 2 | TimeOffAcChg2 | 2512 | U16 | 2 | H:0-23 M:0-59 |  |  |  |  | 是 | yes |  |  | guwDeTimeOffAcChg2 | √ | X | √ | √
AC充电开始时间3 | AC charging start time 3 | TimeOnAcChg3 | 2513 | U16 | 2 | H:0-23 M:0-59 |  |  |  |  | 是 | yes |  |  | guwDeTimeOnAcChg3 | √ | X | √ | √
AC充电结束时间3 | AC charging end time 3 | TimeOffAcChg3 | 2514 | U16 | 2 | H:0-23 M:0-59 |  |  |  |  | 是 | yes |  |  | guwDeTimeOffAcChg3 | √ | X | √ | √
AC充电开始时间4 | AC charging start time 4 | TimeOnAcChg4 | 2515 | U16 | 2 | [6 empty] | #VALUE! |  |  | guwDeTimeOnAcChg4 | √ | X | √ | √
AC充电结束时间4 | AC charging end time 4 | TimeOffAcChg4 | 2516 | U16 | 2 | [6 empty] | #VALUE! |  |  | guwDeTimeOffAcChg4 | √ | X | √ | √
强制充电开始时间1 | Forced charging start time 1 | TimeOnForceChg1 | 2517 | U16 | 2 | H:0-23 M:0-59 |  |  |  |  | 是 | yes |  |  | guwDeTimeOnForceChg1 | √ | X | √ | √
强制充电结束时间1 | Forced charging end time 1 | TimeOffForceChg1 | 2518 | U16 | 2 | H:0-23 M:0-59 |  |  |  |  | 是 | yes |  |  | guwDeTimeOffForceChg1 | √ | X | √ | √
强制充电开始时间2 | Forced charging start time 2 | TimeOnForceChg2 | 2519 | U16 | 2 | H:0-23 M:0-59 |  |  |  |  | 是 | yes |  |  | guwDeTimeOnForceChg2 | √ | X | √ | √
强制充电结束时间2 | Forced charging end time 2 | TimeOffForceChg2 | 2520 | U16 | 2 | H:0-23 M:0-59 |  |  |  |  | 是 | yes |  |  | guwDeTimeOffForceChg2 | √ | X | √ | √
强制充电开始时间3 | Forced charging start time 3 | TimeOnForceChg3 | 2521 | U16 | 2 | H:0-23 M:0-59 |  |  |  |  | 是 | yes |  |  | guwDeTimeOnForceChg3 | √ | X | √ | √
强制充电结束时间3 | Forced charging end time 3 | TimeOffForceChg3 | 2522 | U16 | 2 | H:0-23 M:0-59 |  |  |  |  | 是 | yes |  |  | guwDeTimeOffForceChg3 | √ | X | √ | √
强制充电开始时间4 | Forced charging start time 4 | TimeOnForceChg4 | 2523 | U16 | 2 | [6 empty] | #VALUE! |  |  | guwDeTimeOnForceChg4 | √ | X | √ | √
强制充电结束时间4 | Forced charging end time 4 | TimeOffForceChg4 | 2524 | U16 | 2 | [6 empty] | #VALUE! |  |  | guwDeTimeOffForceChg4 | √ | X | √ | √
强制放电开始时间1 | Forced discharge start time 1 | TimeOnForceDisChg1 | 2525 | U16 | 2 | H:0-23 M:0-59 |  |  |  |  | 是 | yes |  |  | guwDeTimeOnForceDisChg1 | √ | X | √ | √
强制放电结束时间1 | Forced discharge end time 1 | TimeOffForceDisChg1 | 2526 | U16 | 2 | H:0-23 M:0-59 |  |  |  |  | 是 | yes |  |  | guwDeTimeOffForceDisChg1 | √ | X | √ | √
强制放电开始时间2 | Forced discharge start time 2 | TimeOnForceDisChg2 | 2527 | U16 | 2 | H:0-23 M:0-59 |  |  |  |  | 是 | yes |  |  | guwDeTimeOnForceDisChg2 | √ | X | √ | √
强制放电结束时间2 | Forced discharge end time 2 | TimeOffForceDisChg2 | 2528 | U16 | 2 | H:0-23 M:0-59 |  |  |  |  | 是 | yes |  |  | guwDeTimeOffForceDisChg2 | √ | X | √ | √
强制放电开始时间3 | Forced discharge start time 3 | TimeOnForceDisChg3 | 2529 | U16 | 2 | H:0-23 M:0-59 |  |  |  |  | 是 | yes |  |  | guwDeTimeOnForceDisChg3 | √ | X | √ | √
强制放电结束时间3 | Forced discharge end time 3 | TimeOffForceDisChg3 | 2530 | U16 | 2 | H:0-23 M:0-59 |  |  |  |  | 是 | yes |  |  | guwDeTimeOffForceDisChg3 | √ | X | √ | √
强制放电开始时间4 | Forced discharge start time 4 | TimeOnForceDisChg4 | 2531 | U16 | 2 | [6 empty] | #VALUE! |  |  | guwDeTimeOnForceDisChg4 | √ | X | √ | √
强制放电结束时间4 | Forced discharge end time 4 | TimeOffForceDisChg4 | 2532 | U16 | 2 | [6 empty] | #VALUE! |  |  | guwDeTimeOffForceDisChg4 | √ | X | √ | √
禁止放电开始时间1 | Discharge prohibition start time 1 | TimeOnForbidChg1 | 2533 | U16 | 2 | H:0-23 M:0-59 |  |  |  |  | 是 | yes |  |  | guwDeTimeOnForbidChg1 | √ | X | √ | √
禁止放电结束时间1 | Discharge prohibited end time 1 | TimeOffForbidChg1 | 2534 | U16 | 2 | H:0-23 M:0-59 |  |  |  |  | 是 | yes |  |  | guwDeTimeOffForbidChg1 | √ | X | √ | √
禁止放电开始时间2 | Discharge prohibition start time 2 | TimeOnForbidChg2 | 2535 | U16 | 2 | H:0-23 M:0-59 |  |  |  |  | 是 | yes |  |  | guwDeTimeOnForbidChg2 | √ | X | √ | √
禁止放电结束时间2 | Discharge prohibition end time 2 | TimeOffForbidChg2 | 2536 | U16 | 2 | H:0-23 M:0-59 |  |  |  |  | 是 | yes |  |  | guwDeTimeOffForbidChg2 | √ | X | √ | √
禁止放电开始时间3 | Discharge prohibition start time 3 | TimeOnForbidChg3 | 2537 | U16 | 2 | H:0-23 M:0-59 |  |  |  |  | 是 | yes |  |  | guwDeTimeOnForbidChg3 | √ | X | √ | √
禁止放电结束时间3 | Discharge prohibition end time 3 | TimeOffForbidChg3 | 2538 | U16 | 2 | H:0-23 M:0-59 |  |  |  |  | 是 | yes |  |  | guwDeTimeOffForbidChg3 | √ | X | √ | √
禁止放电开始时间4 | Discharge prohibition start time 4 | TimeOnForbidChg4 | 2539 | U16 | 2 | [6 empty] | #VALUE! |  |  | guwDeTimeOnForbidChg4 | √ | X | √ | √
禁止放电结束时间4 | Discharge prohibition end time 4 | TimeOffForbidChg4 | 2540 | U16 | 2 | [6 empty] | #VALUE! |  |  | guwDeTimeOffForbidChg4 | √ | X | √ | √
负载调节模式 | load regulation mode | LoadCtrlMode | 2541 | U16 | 2 | 0：开关模式 1：定时模式 2：智能模式 3：关闭 | 0: switch mode 1: Timing mode 2: Intelligent mode 3: Close |  |  |  | 是 | yes |  |  | guwDeLoadCtrlMode | √ | X | √ | √
负载开时间1 | Load on time 1 | TimeOnLoad1 | 2542 | U16 | 2 | [6 empty] | #VALUE! |  |  | guwDeTimeOnLoad1 | √ | X | √ | √
负载关时间1 | Load off time 1 | TimeOffLoad1 | 2543 | U16 | 2 | [6 empty] | #VALUE! |  |  | guwDeTimeOffLoad1 | √ | X | √ | √
负载开时间2 | Load on time 2 | TimeOnLoad2 | 2544 | U16 | 2 | [6 empty] | #VALUE! |  |  | guwDeTimeOnLoad2 | √ | X | √ | √
负载关时间2 | Load off time 2 | TimeOffLoad2 | 2545 | U16 | 2 | [6 empty] | #VALUE! |  |  | guwDeTimeOffLoad2 | √ | X | √ | √
负载额定功率 | Load rated power | NormLoadPower | 2546-2547 | U32 | 4 | [5 empty] | 是 | yes |  |  | gulDeNormLoadPower | √ | X | √ | √
强制充电最大SOC | Forced charging maximum SOC | ForceSocMaxChg | 2548 | U16 | 2 | 0-100 |  | % |  |  | 是 | yes |  |  | guwForceSocMaxChg | √ | X | √ | √
预留 | reserved | Reserve | 2549-2999 | [8 empty] | #VALUE! |  |  |  | √ | X | √ | √
设置参数7（电池参数） | Set parameter 7 (battery parameters) | [10 empty] | #VALUE! |  |  |  | √ | X | √ | √
电池类型 | Battery Type | BatType | 3000 | U16 | 2 |  |  |  | 0: 无电池 1:锂电池, 2:铅酸电池 3:模拟电池 | 0: No battery 1: Lithium battery, 2: Lead-acid battery 3: Analog battery | 是 | yes |  |  | guwDeBatType | √ | X | √ | √
锂电池厂家 | Lithium battery manufacturer | BatBrand | 3001 | U16 | 2 | [5 empty] | 是 | yes |  |  | guwDeBatBrand | √ | X | √ | √
电池额定电压 | Battery rated voltage | VBatNorm | 3002 | U16 | 2 | 480-4000 |  | 0.1V |  |  | 是 | yes |  |  | guwDeVBatNorm | √ | X | √ | √
电池容量 | battery capacity | BatCap | 3003 | U16 | 2 | 10~1000 |  | Ah |  |  | 是 | yes |  |  | guwDeBatCap | √ | X | √ | √
允许日充放电次数 | Allowed number of daily charges and discharges | ChgCntMax | 3004 | U16 | 2 | 1-10 |  |  |  |  | 是 | yes |  |  | guwDeChgCntMax | √ | X | √ | √
SOC上限 | SOC upper limit | MaxSOC | 3005 | U16 | 2 | 700~1000 |  | 0.1% |  |  | 是 | yes |  |  | guwDeMaxSOC | √ | X | √ | √
SOC下限 | SOC lower limit | MinSOC | 3006 | U16 | 2 | 0~500 |  | 0.1% |  |  | 是 | yes |  |  | guwDeMinSOC | √ | X | √ | √
电池过压阀值 | Battery overvoltage threshold | VBatMax | 3007 | U16 | 2 | 480~4500 |  | 0.1V |  |  | 是 | yes |  |  | guwDeVBatMax | √ | X | √ | √
电池欠压阀值 | Battery undervoltage threshold | VBatMin | 3008 | U16 | 2 | 300~4000 |  | 0.1V |  |  | 是 | yes |  |  | guwDeVBatMin | √ | X | √ | √
最大充电电流 | Maximum charging current | CurrMaxChg | 3009 | U16 | 2 | 50~2000 南都默认250，三星默认1000 | 50~2000 Nandu defaults to 250, Samsung defaults to 1000 | 0.01A |  |  | 是 | yes |  |  | guwDeCurrMaxChg | √ | X | √ | √
最大放电电流 | Maximum discharge current | CurrMaxDisChg | 3010 | U16 | 2 | 100~2000C 默认1000 | 100~2000C default 1000 | 0.01A |  |  | 是 | yes |  |  | guwDeCurrMaxDisChg | √ | X | √ | √
电池过温阀值 | Battery over temperature threshold | TBatMax | 3011 | S16 | 2 | 200~850 默认600 | 200~850 Default 600 | 0.1℃ |  |  | 是 | yes |  |  | gwDeTBatMax | √ | X | √ | √
电池欠温阀值 | Battery under-temperature threshold | TBatMin | 3012 | S16 | 2 | (-300~100) 默认-20.0 | (-300~100) Default -20.0 | 0.1℃ |  |  | 是 | yes |  |  | gwDeTBatMin | √ | X | √ | √
恒压充电电压 | Constant charging voltage | VConstVolt | 3013 | U16 | 2 | 400~4500 |  | 0.1V |  |  | 是 | yes |  |  | guwDeVConstVolt | √ | X | √ | √
恒压充电终止电流 | Constant voltage charge termination current | IConstVoltEnd | 3014 | U16 | 2 | 500~5000 |  | 0.01A |  |  | 是 | yes |  |  | guwDeIConstVoltEnd | √ | X | √ | √
恒压充电时间 | Constant voltage charging time | TConstVolt | 3015 | U16 | 2 | 300~4500V |  | 0.1V |  |  | 是 | yes |  |  | guwDeTConstVolt | √ | X | √ | √
放电终止电压 | Discharge termination voltage | VDisChgEnd | 3016 | U16 | 2 | 300~4500V |  | 0.1V |  |  | 是 | yes |  |  | guwDeVDisChgEnd | √ | X | √ | √
紧急充电启动电压 | Emergency charging starting voltage | EmerChgStartV | 3017 | U16 | 2 | 400-4500 |  | 0.1V |  |  |  | #VALUE! |  |  | guwDeEmerChgStartV | √ | X | √ | √
紧急充电停止电压 | Emergency charging stop voltage | EmerChgEndV | 3018 | U16 | 2 | 400-4500 |  | 0.1V |  |  |  | #VALUE! |  |  | guwDeEmerChgEndV | √ | X | √ | √
紧急充电电流 | Emergency charging current | EmerChgI | 3019 | U16 | 2 | 25~2000 |  | 0.01A |  |  | 是 | yes |  |  | guwDeEmerChgI | √ | X | √ | √
电阻补偿 | Resistor compensation | BatResComp | 3020 | S16 | 2 | 0.0~50000 |  | 0.1mΩ |  |  | 是 | yes |  |  | gwDeBatResComp | √ | X | √ | √
温度补偿 | temperature compensation | BatTempComp | 3021 | S16 | 2 |  |  | 0.1℃ |  |  | 是 | yes |  |  | gwDeBatTempComp | √ | X | √ | √
最大充电功率 | Maximum charging power | WChaMax | 3022-3023 | U32 | 4 | 100~100000 |  | 1W |  |  | 是 | yes |  |  | gwDeWChaMax | √ | X | √ | √
最大充电变化率 | Maximum charge change rate | WChaGra | 3024 | U16 | 2 | 0~1000 |  | % |  |  | 是 | yes |  |  | gwDeWChaGra | √ | X | √ | √
最大放点变化率 | Maximum release point change rate | WDisChaGra | 3025 | U16 | 2 | 0~1000 |  | % |  |  | 是 | yes |  |  | gwDeWDisChaGra | √ | X | √ | √
铅酸电池厂家 | Lead-acid battery manufacturers | LeadAcidBrand | 3026 | U16 |  | 0. common 1. SACRED 圣阳 2. | 0.common 1. SACRED 2.
预留 |  | Reserve | 3027-3499 | [12 empty] | √ | X | √ | √

## 国家-nation
国家 | 编码 | 备注
Com_50Hz | 0 | 50Hz宽范围参数 | 50Hz wide range parameters
Com_60Hz | 1 | 60Hz宽范围参数 | 60Hz wide range parameters
CN | 2 | 中国 | China
JP_50Hz | 3 | 日本50Hz电网 | Japan 50Hz power grid
JP_60Hz | 4 | 日本60Hz电网 | Japan 60Hz power grid
US_240S | 5 | 美国240V单相 | American 240V single phase
US_240D | 6 | 美国240V裂相 | American 240V split phase
US_208S | 7 | 美国208V单相 | American 208V single phase
US_208D | 8 | 美国208V裂相 | American 208V split phase
AU | 9 | 澳大利亚 | Australia
UK_G83 | 10 | 英国G83标准 | British G83 standard
UK_G59 | 11 | 英国G59标准 | British G59 standard
DE | 12 | 德国低压电网 | German low voltage power grid
DE_BDEW | 13 | 德国中压电网 | German medium voltage power grid
FR | 14 | 法国 | France
FR_IL50Hz | 15 | 法国50Hz岛屿 | French 50Hz Island
FR_IL60Hz | 16 | 法国60Hz岛屿 | French 60Hz Island
PL | 17 | 波兰 | Poland
IT | 18 | 意大利 | Italy
TH_ME | 19 | 泰国ME地区 | Thailand ME region
TH_PE | 20 | 泰国PE地区 | Thailand PE region
IN | 21 | 印度 | India
KR | 22 | 韩国 | South Korea
PH | 23 | 菲律宾 | the Philippines
KP | 24 | 朝鲜 | North Korea
MY | 25 | 马来西亚 | Malaysia
CY | 26 | 塞浦路斯 | Cyprus
NL | 27 | 荷兰 | Netherlands
NL_16A | 28 | 荷兰限制16A并网 | Netherlands restricts 16A grid connection
ES | 29 | 西班牙 | Spain
GR | 30 | 希腊 | Greece
GR_IL | 31 | 希腊岛屿 | greek islands
PT | 32 | 葡萄牙 | Portugal
BE | 33 | 比利时 | Belgium
DK | 34 | 丹麦 | Denmark
DK_16A | 35 | 丹麦限制16A并网 | Denmark restricts 16A grid connection
CZ | 36 | 捷克 | Czech Republic
SK | 37 | 斯洛伐克 | Slovakia
SE | 38 | 瑞典 | Sweden
AT | 39 | 奥地利 | Austria
BG | 40 | 保加利亚 | Bulgaria
RO | 41 | 罗马尼亚 | Romania
UA | 42 | 乌克兰 | Ukraine
ZA | 43 | 南非 | South Africa
MU | 44 | 毛里求斯 | Mauritius
IL | 45 | 以色列 | Israel
MX | 46 | 墨西哥 | Mexico
BR | 47 | 巴西 | Brazil
LK | 48 | 斯里兰卡 | Sri Lanka
CL | 49 | 智利 | Chile
CONNERA | 50 | 墨西哥CONNERA定制 | Mexico CONNERA customization